## Sheet1
Location | RTU | Time | NameOfCheck
WLLS1 | RTU1 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU1 | 2024-01-11 17:29:46 | Short Cycling Detected
WLLS1 | RTU1 | 2024-01-11 17:59:48 | Short Cycling Detected
WLLS1 | RTU1 | 2024-03-13 23:14:52 | Short Cycling Detected
WLLS1 | RTU1 | 2024-01-06 14:59:54 | Compressor run ignoring free cooling Opportunity of 3.61 kWh | No
WLLS1 | RTU1 | 2024-01-06 15:14:48 | Compressor run ignoring free cooling Opportunity of 4.91 kWh
WLLS1 | RTU1 | 2024-01-06 17:00:01 | Compressor run ignoring free cooling Opportunity of 4.66 kWh
WLLS1 | RTU1 | 2024-01-06 17:14:56 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-01-06 17:29:53 | Compressor run ignoring free cooling Opportunity of 4.51 kWh
WLLS1 | RTU1 | 2024-01-06 17:44:50 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-01-06 19:29:59 | Compressor run ignoring free cooling Opportunity of 4.82 kWh
WLLS1 | RTU1 | 2024-01-06 19:44:54 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-01-06 19:59:51 | Compressor run ignoring free cooling Opportunity of 4.68 kWh
WLLS1 | RTU1 | 2024-01-06 20:14:47 | Compressor run ignoring free cooling Opportunity of 5.00 kWh
WLLS1 | RTU1 | 2024-01-09 11:14:57 | Compressor run ignoring free cooling Opportunity of 4.22 kWh
WLLS1 | RTU1 | 2024-01-09 12:15:01 | Compressor run ignoring free cooling Opportunity of 4.84 kWh
WLLS1 | RTU1 | 2024-01-09 13:30:00 | Compressor run ignoring free cooling Opportunity of 4.62 kWh
WLLS1 | RTU1 | 2024-01-09 14:44:53 | Compressor run ignoring free cooling Opportunity of 8.54 kWh
WLLS1 | RTU1 | 2024-01-09 15:44:57 | Compressor run ignoring free cooling Opportunity of 10.28 kWh
WLLS1 | RTU1 | 2024-01-09 17:59:51 | Compressor run ignoring free cooling Opportunity of 10.24 kWh
WLLS1 | RTU1 | 2024-01-09 18:59:57 | Compressor run ignoring free cooling Opportunity of 3.23 kWh
WLLS1 | RTU1 | 2024-01-09 20:14:55 | Compressor run ignoring free cooling Opportunity of 9.48 kWh
WLLS1 | RTU1 | 2024-01-11 13:44:57 | Compressor run ignoring free cooling Opportunity of 3.10 kWh
WLLS1 | RTU1 | 2024-01-16 18:14:43 | Compressor run ignoring free cooling Opportunity of 3.15 kWh
WLLS1 | RTU1 | 2024-01-16 18:29:47 | Compressor run ignoring free cooling Opportunity of 3.10 kWh
WLLS1 | RTU1 | 2024-01-16 18:44:49 | Compressor run ignoring free cooling Opportunity of 3.10 kWh
WLLS1 | RTU1 | 2024-01-16 18:59:52 | Compressor run ignoring free cooling Opportunity of 3.08 kWh
WLLS1 | RTU1 | 2024-01-16 19:14:52 | Compressor run ignoring free cooling Opportunity of 3.57 kWh
WLLS1 | RTU1 | 2024-01-16 19:29:53 | Compressor run ignoring free cooling Opportunity of 3.81 kWh
WLLS1 | RTU1 | 2024-01-16 19:44:53 | Compressor run ignoring free cooling Opportunity of 3.26 kWh
WLLS1 | RTU1 | 2024-01-16 19:59:53 | Compressor run ignoring free cooling Opportunity of 3.19 kWh
WLLS1 | RTU1 | 2024-01-16 20:14:53 | Compressor run ignoring free cooling Opportunity of 4.51 kWh
WLLS1 | RTU1 | 2024-01-19 17:59:43 | Compressor run ignoring free cooling Opportunity of 5.20 kWh
WLLS1 | RTU1 | 2024-01-19 18:14:44 | Compressor run ignoring free cooling Opportunity of 5.20 kWh
WLLS1 | RTU1 | 2024-01-19 18:29:45 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-01-24 13:29:59 | Compressor run ignoring free cooling Opportunity of 5.98 kWh
WLLS1 | RTU1 | 2024-01-24 15:29:59 | Compressor run ignoring free cooling Opportunity of 5.89 kWh
WLLS1 | RTU1 | 2024-01-24 17:29:58 | Compressor run ignoring free cooling Opportunity of 6.07 kWh
WLLS1 | RTU1 | 2024-01-24 18:45:01 | Compressor run ignoring free cooling Opportunity of 5.76 kWh
WLLS1 | RTU1 | 2024-01-24 20:45:00 | Compressor run ignoring free cooling Opportunity of 5.82 kWh
WLLS1 | RTU1 | 2024-01-24 23:29:55 | Compressor run ignoring free cooling Opportunity of 5.87 kWh
WLLS1 | RTU1 | 2024-01-24 23:45:00 | Compressor run ignoring free cooling Opportunity of 5.89 kWh
WLLS1 | RTU1 | 2024-01-24 23:59:40 | Compressor run ignoring free cooling Opportunity of 5.87 kWh
WLLS1 | RTU1 | 2024-01-25 03:29:58 | Compressor run ignoring free cooling Opportunity of 6.00 kWh
WLLS1 | RTU1 | 2024-01-25 04:59:43 | Compressor run ignoring free cooling Opportunity of 5.96 kWh
WLLS1 | RTU1 | 2024-01-25 15:14:59 | Compressor run ignoring free cooling Opportunity of 10.93 kWh
WLLS1 | RTU1 | 2024-01-25 20:29:59 | Compressor run ignoring free cooling Opportunity of 9.73 kWh
WLLS1 | RTU1 | 2024-01-25 22:30:00 | Compressor run ignoring free cooling Opportunity of 10.91 kWh
WLLS1 | RTU1 | 2024-01-26 09:59:59 | Compressor run ignoring free cooling Opportunity of 10.53 kWh
WLLS1 | RTU1 | 2024-01-26 16:44:59 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-01-26 17:44:58 | Compressor run ignoring free cooling Opportunity of 10.46 kWh
WLLS1 | RTU1 | 2024-01-26 18:44:56 | Compressor run ignoring free cooling Opportunity of 10.71 kWh
WLLS1 | RTU1 | 2024-01-26 19:44:53 | Compressor run ignoring free cooling Opportunity of 10.51 kWh
WLLS1 | RTU1 | 2024-01-26 21:30:00 | Compressor run ignoring free cooling Opportunity of 10.31 kWh
WLLS1 | RTU1 | 2024-01-26 22:30:00 | Compressor run ignoring free cooling Opportunity of 9.81 kWh
WLLS1 | RTU1 | 2024-01-26 23:59:58 | Compressor run ignoring free cooling Opportunity of 9.99 kWh
WLLS1 | RTU1 | 2024-01-27 14:14:53 | Compressor run ignoring free cooling Opportunity of 9.70 kWh
WLLS1 | RTU1 | 2024-01-27 17:14:53 | Compressor run ignoring free cooling Opportunity of 4.84 kWh
WLLS1 | RTU1 | 2024-02-14 17:14:58 | Compressor run ignoring free cooling Opportunity of 4.22 kWh
WLLS1 | RTU1 | 2024-02-15 16:14:58 | Compressor run ignoring free cooling Opportunity of 3.21 kWh
WLLS1 | RTU1 | 2024-02-20 17:45:00 | Compressor run ignoring free cooling Opportunity of 3.15 kWh
WLLS1 | RTU1 | 2024-02-20 18:29:59 | Compressor run ignoring free cooling Opportunity of 2.99 kWh
WLLS1 | RTU1 | 2024-02-22 14:14:58 | Compressor run ignoring free cooling Opportunity of 3.66 kWh
WLLS1 | RTU1 | 2024-02-22 16:15:00 | Compressor run ignoring free cooling Opportunity of 3.19 kWh
WLLS1 | RTU1 | 2024-02-22 19:00:00 | Compressor run ignoring free cooling Opportunity of 2.99 kWh
WLLS1 | RTU1 | 2024-02-23 18:00:00 | Compressor run ignoring free cooling Opportunity of 4.60 kWh
WLLS1 | RTU1 | 2024-02-26 16:29:57 | Compressor run ignoring free cooling Opportunity of 3.17 kWh
WLLS1 | RTU1 | 2024-02-26 19:14:58 | Compressor run ignoring free cooling Opportunity of 3.15 kWh
WLLS1 | RTU1 | 2024-02-27 14:14:46 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-02-27 17:44:59 | Compressor run ignoring free cooling Opportunity of 4.80 kWh
WLLS1 | RTU1 | 2024-02-28 09:14:57 | Compressor run ignoring free cooling Opportunity of 3.61 kWh
WLLS1 | RTU1 | 2024-02-28 14:29:59 | Compressor run ignoring free cooling Opportunity of 10.44 kWh
WLLS1 | RTU1 | 2024-02-28 17:14:59 | Compressor run ignoring free cooling Opportunity of 8.81 kWh
WLLS1 | RTU1 | 2024-02-28 20:44:57 | Compressor run ignoring free cooling Opportunity of 7.79 kWh
WLLS1 | RTU1 | 2024-03-01 16:15:00 | Compressor run ignoring free cooling Opportunity of 3.21 kWh
WLLS1 | RTU1 | 2024-03-03 14:29:58 | Compressor run ignoring free cooling Opportunity of 9.99 kWh
WLLS1 | RTU1 | 2024-03-03 16:30:01 | Compressor run ignoring free cooling Opportunity of 9.99 kWh
WLLS1 | RTU1 | 2024-03-03 22:00:01 | Compressor run ignoring free cooling Opportunity of 4.82 kWh
WLLS1 | RTU1 | 2024-03-04 10:44:43 | Compressor run ignoring free cooling Opportunity of 4.55 kWh
WLLS1 | RTU1 | 2024-03-04 12:45:01 | Compressor run ignoring free cooling Opportunity of 8.30 kWh
WLLS1 | RTU1 | 2024-03-04 12:59:55 | Compressor run ignoring free cooling Opportunity of 10.28 kWh
WLLS1 | RTU1 | 2024-03-04 13:14:51 | Compressor run ignoring free cooling Opportunity of 10.02 kWh
WLLS1 | RTU1 | 2024-03-04 13:29:47 | Compressor run ignoring free cooling Opportunity of 10.22 kWh
WLLS1 | RTU1 | 2024-03-04 15:15:01 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-03-04 15:29:55 | Compressor run ignoring free cooling Opportunity of 4.82 kWh
WLLS1 | RTU1 | 2024-03-04 15:44:51 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-03-04 15:59:47 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-03-04 17:30:00 | Compressor run ignoring free cooling Opportunity of 9.93 kWh
WLLS1 | RTU1 | 2024-03-04 17:44:55 | Compressor run ignoring free cooling Opportunity of 4.68 kWh
WLLS1 | RTU1 | 2024-03-04 17:59:49 | Compressor run ignoring free cooling Opportunity of 4.24 kWh
WLLS1 | RTU1 | 2024-03-04 20:00:00 | Compressor run ignoring free cooling Opportunity of 4.55 kWh
WLLS1 | RTU1 | 2024-03-04 20:14:56 | Compressor run ignoring free cooling Opportunity of 4.44 kWh
WLLS1 | RTU1 | 2024-03-04 20:29:51 | Compressor run ignoring free cooling Opportunity of 4.68 kWh
WLLS1 | RTU1 | 2024-03-04 22:15:00 | Compressor run ignoring free cooling Opportunity of 5.09 kWh
WLLS1 | RTU1 | 2024-03-04 22:29:57 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-03-04 22:44:53 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-03-04 22:59:48 | Compressor run ignoring free cooling Opportunity of 4.66 kWh
WLLS1 | RTU1 | 2024-03-05 10:14:56 | Compressor run ignoring free cooling Opportunity of 4.57 kWh
WLLS1 | RTU1 | 2024-03-05 12:29:58 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-03-05 12:44:53 | Compressor run ignoring free cooling Opportunity of 4.66 kWh
WLLS1 | RTU1 | 2024-03-05 14:45:02 | Compressor run ignoring free cooling Opportunity of 9.84 kWh
WLLS1 | RTU1 | 2024-03-05 14:59:59 | Compressor run ignoring free cooling Opportunity of 10.02 kWh
WLLS1 | RTU1 | 2024-03-05 15:14:56 | Compressor run ignoring free cooling Opportunity of 10.19 kWh
WLLS1 | RTU1 | 2024-03-05 15:29:52 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-03-05 15:44:47 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU1 | 2024-03-05 17:30:01 | Compressor run ignoring free cooling Opportunity of 4.82 kWh
WLLS1 | RTU1 | 2024-03-05 17:44:56 | Compressor run ignoring free cooling Opportunity of 7.92 kWh
WLLS1 | RTU1 | 2024-03-05 17:59:50 | Compressor run ignoring free cooling Opportunity of 4.68 kWh
WLLS1 | RTU1 | 2024-03-05 19:59:58 | Compressor run ignoring free cooling Opportunity of 4.60 kWh
WLLS1 | RTU1 | 2024-03-05 20:14:53 | Compressor run ignoring free cooling Opportunity of 4.84 kWh
WLLS1 | RTU1 | 2024-03-05 20:29:50 | Compressor run ignoring free cooling Opportunity of 8.28 kWh
WLLS1 | RTU1 | 2024-03-06 11:14:59 | Compressor run ignoring free cooling Opportunity of 4.64 kWh
WLLS1 | RTU1 | 2024-03-06 11:29:55 | Compressor run ignoring free cooling Opportunity of 5.20 kWh
WLLS1 | RTU1 | 2024-03-06 11:44:51 | Compressor run ignoring free cooling Opportunity of 5.20 kWh
WLLS1 | RTU1 | 2024-03-06 11:59:47 | Compressor run ignoring free cooling Opportunity of 5.35 kWh
WLLS1 | RTU1 | 2024-03-06 13:45:01 | Compressor run ignoring free cooling Opportunity of 4.89 kWh
WLLS1 | RTU1 | 2024-03-06 13:59:55 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-03-06 14:14:50 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-03-06 16:00:01 | Compressor run ignoring free cooling Opportunity of 8.52 kWh
WLLS1 | RTU1 | 2024-03-06 16:14:57 | Compressor run ignoring free cooling Opportunity of 10.33 kWh
WLLS1 | RTU1 | 2024-03-06 16:29:53 | Compressor run ignoring free cooling Opportunity of 5.24 kWh
WLLS1 | RTU1 | 2024-03-06 16:44:47 | Compressor run ignoring free cooling Opportunity of 5.20 kWh
WLLS1 | RTU1 | 2024-03-06 18:44:59 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-03-06 18:59:56 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-03-06 19:14:52 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-03-06 19:29:46 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-03-07 07:29:58 | Compressor run ignoring free cooling Opportunity of 5.00 kWh
WLLS1 | RTU1 | 2024-03-07 07:44:54 | Compressor run ignoring free cooling Opportunity of 4.68 kWh
WLLS1 | RTU1 | 2024-03-07 07:59:48 | Compressor run ignoring free cooling Opportunity of 4.91 kWh
WLLS1 | RTU1 | 2024-03-07 08:14:44 | Compressor run ignoring free cooling Opportunity of 4.64 kWh
WLLS1 | RTU1 | 2024-03-07 09:59:59 | Compressor run ignoring free cooling Opportunity of 10.51 kWh
WLLS1 | RTU1 | 2024-03-07 10:14:55 | Compressor run ignoring free cooling Opportunity of 8.92 kWh
WLLS1 | RTU1 | 2024-03-07 10:29:49 | Compressor run ignoring free cooling Opportunity of 10.35 kWh
WLLS1 | RTU1 | 2024-03-07 12:29:58 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-03-07 12:44:53 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-03-07 12:59:50 | Compressor run ignoring free cooling Opportunity of 9.57 kWh
WLLS1 | RTU1 | 2024-03-07 13:14:47 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-03-07 14:59:59 | Compressor run ignoring free cooling Opportunity of 8.52 kWh
WLLS1 | RTU1 | 2024-03-07 15:44:47 | Compressor run ignoring free cooling Opportunity of 10.60 kWh
WLLS1 | RTU1 | 2024-03-07 17:30:01 | Compressor run ignoring free cooling Opportunity of 10.91 kWh
WLLS1 | RTU1 | 2024-03-07 17:44:55 | Compressor run ignoring free cooling Opportunity of 8.50 kWh
WLLS1 | RTU1 | 2024-03-07 17:59:50 | Compressor run ignoring free cooling Opportunity of 5.26 kWh
WLLS1 | RTU1 | 2024-03-07 18:14:48 | Compressor run ignoring free cooling Opportunity of 4.89 kWh
WLLS1 | RTU1 | 2024-03-07 20:14:58 | Compressor run ignoring free cooling Opportunity of 4.64 kWh
WLLS1 | RTU1 | 2024-03-07 20:29:54 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-03-07 20:44:48 | Compressor run ignoring free cooling Opportunity of 5.02 kWh
WLLS1 | RTU1 | 2024-03-07 22:29:59 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-03-07 22:44:54 | Compressor run ignoring free cooling Opportunity of 4.91 kWh
WLLS1 | RTU1 | 2024-03-07 23:59:58 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-03-08 13:44:59 | Compressor run ignoring free cooling Opportunity of 4.62 kWh
WLLS1 | RTU1 | 2024-03-08 13:59:54 | Compressor run ignoring free cooling Opportunity of 4.89 kWh
WLLS1 | RTU1 | 2024-03-08 14:14:53 | Compressor run ignoring free cooling Opportunity of 4.60 kWh
WLLS1 | RTU1 | 2024-03-08 14:29:50 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-03-08 16:30:01 | Compressor run ignoring free cooling Opportunity of 4.48 kWh
WLLS1 | RTU1 | 2024-03-08 16:44:56 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-03-08 16:59:51 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-03-08 17:14:47 | Compressor run ignoring free cooling Opportunity of 3.30 kWh
WLLS1 | RTU1 | 2024-03-08 18:45:02 | Compressor run ignoring free cooling Opportunity of 4.62 kWh
WLLS1 | RTU1 | 2024-03-08 18:59:56 | Compressor run ignoring free cooling Opportunity of 4.91 kWh
WLLS1 | RTU1 | 2024-03-08 19:14:51 | Compressor run ignoring free cooling Opportunity of 4.60 kWh
WLLS1 | RTU1 | 2024-03-08 21:44:50 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-03-09 13:59:46 | Compressor run ignoring free cooling Opportunity of 9.75 kWh
WLLS1 | RTU1 | 2024-03-09 14:44:40 | Compressor run ignoring free cooling Opportunity of 9.68 kWh
WLLS1 | RTU1 | 2024-03-09 20:44:41 | Compressor run ignoring free cooling Opportunity of 9.46 kWh
WLLS1 | RTU1 | 2024-03-09 22:29:43 | Compressor run ignoring free cooling Opportunity of 9.59 kWh
WLLS1 | RTU1 | 2024-03-12 17:44:48 | Compressor run ignoring free cooling Opportunity of 3.10 kWh
WLLS1 | RTU1 | 2024-03-12 19:30:01 | Compressor run ignoring free cooling Opportunity of 3.17 kWh
WLLS1 | RTU1 | 2024-03-12 19:44:56 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-03-12 19:59:54 | Compressor run ignoring free cooling Opportunity of 3.15 kWh
WLLS1 | RTU1 | 2024-03-12 20:14:49 | Compressor run ignoring free cooling Opportunity of 3.17 kWh
WLLS1 | RTU1 | 2024-03-13 20:14:57 | Compressor run ignoring free cooling Opportunity of 3.08 kWh
WLLS1 | RTU1 | 2024-03-13 20:29:54 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-03-13 20:44:49 | Compressor run ignoring free cooling Opportunity of 3.30 kWh
WLLS1 | RTU1 | 2024-03-13 20:59:46 | Compressor run ignoring free cooling Opportunity of 3.10 kWh
WLLS1 | RTU1 | 2024-03-14 19:29:53 | Compressor run ignoring free cooling Opportunity of 3.15 kWh
WLLS1 | RTU1 | 2024-03-14 19:44:49 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-03-14 19:59:44 | Compressor run ignoring free cooling Opportunity of 3.08 kWh
WLLS1 | RTU1 | 2024-03-14 21:59:58 | Compressor run ignoring free cooling Opportunity of 4.84 kWh
WLLS1 | RTU1 | 2024-03-14 22:14:55 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-03-14 22:29:53 | Compressor run ignoring free cooling Opportunity of 4.89 kWh
WLLS1 | RTU1 | 2024-03-14 22:44:48 | Compressor run ignoring free cooling Opportunity of 3.15 kWh
WLLS1 | RTU1 | 2024-03-14 23:45:01 | Compressor run ignoring free cooling Opportunity of 3.10 kWh
WLLS1 | RTU1 | 2024-03-15 01:59:58 | Compressor run ignoring free cooling Opportunity of 3.10 kWh
WLLS1 | RTU1 | 2024-03-15 02:14:53 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-03-15 02:29:49 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-03-15 04:29:58 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-03-15 06:29:50 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU1 | 2024-03-15 08:30:01 | Compressor run ignoring free cooling Opportunity of 2.92 kWh
WLLS1 | RTU1 | 2024-03-15 08:44:56 | Compressor run ignoring free cooling Opportunity of 4.39 kWh
WLLS1 | RTU1 | 2024-03-15 08:59:50 | Compressor run ignoring free cooling Opportunity of 2.94 kWh
WLLS1 | RTU1 | 2024-03-15 10:45:00 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-03-15 15:44:59 | Compressor run ignoring free cooling Opportunity of 9.57 kWh
WLLS1 | RTU1 | 2024-03-15 15:59:54 | Compressor run ignoring free cooling Opportunity of 10.84 kWh
WLLS1 | RTU1 | 2024-03-15 16:14:50 | Compressor run ignoring free cooling Opportunity of 10.84 kWh
WLLS1 | RTU1 | 2024-03-15 18:14:56 | Compressor run ignoring free cooling Opportunity of 10.73 kWh
WLLS1 | RTU1 | 2024-03-15 18:29:51 | Compressor run ignoring free cooling Opportunity of 5.06 kWh
WLLS1 | RTU1 | 2024-03-15 18:44:48 | Compressor run ignoring free cooling Opportunity of 11.11 kWh
WLLS1 | RTU1 | 2024-03-15 20:45:00 | Compressor run ignoring free cooling Opportunity of 10.42 kWh
WLLS1 | RTU1 | 2024-03-15 20:59:54 | Compressor run ignoring free cooling Opportunity of 10.48 kWh
WLLS1 | RTU1 | 2024-03-15 21:14:49 | Compressor run ignoring free cooling Opportunity of 8.03 kWh
WLLS1 | RTU1 | 2024-03-15 21:29:45 | Compressor run ignoring free cooling Opportunity of 4.82 kWh
WLLS1 | RTU1 | 2024-03-15 23:00:00 | Compressor run ignoring free cooling Opportunity of 4.97 kWh
WLLS1 | RTU1 | 2024-03-15 23:14:55 | Compressor run ignoring free cooling Opportunity of 4.71 kWh
WLLS1 | RTU1 | 2024-03-16 00:14:54 | Compressor run ignoring free cooling Opportunity of 8.23 kWh
WLLS1 | RTU1 | 2024-03-16 00:29:49 | Compressor run ignoring free cooling Opportunity of 4.82 kWh
WLLS1 | RTU1 | 2024-03-16 02:29:58 | Compressor run ignoring free cooling Opportunity of 9.75 kWh
WLLS1 | RTU1 | 2024-03-16 02:44:55 | Compressor run ignoring free cooling Opportunity of 9.90 kWh
WLLS1 | RTU1 | 2024-03-16 02:59:53 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-03-16 03:14:47 | Compressor run ignoring free cooling Opportunity of 9.75 kWh
WLLS1 | RTU1 | 2024-03-16 06:59:57 | Compressor run ignoring free cooling Opportunity of 4.57 kWh
WLLS1 | RTU1 | 2024-03-16 07:14:53 | Compressor run ignoring free cooling Opportunity of 7.85 kWh
WLLS1 | RTU1 | 2024-03-16 07:29:49 | Compressor run ignoring free cooling Opportunity of 10.08 kWh
WLLS1 | RTU1 | 2024-03-16 09:30:00 | Compressor run ignoring free cooling Opportunity of 4.46 kWh
WLLS1 | RTU1 | 2024-03-16 09:44:54 | Compressor run ignoring free cooling Opportunity of 4.66 kWh
WLLS1 | RTU1 | 2024-03-16 09:59:50 | Compressor run ignoring free cooling Opportunity of 4.55 kWh
WLLS1 | RTU1 | 2024-03-16 10:14:48 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-03-16 12:00:01 | Compressor run ignoring free cooling Opportunity of 4.64 kWh
WLLS1 | RTU1 | 2024-03-16 12:14:56 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-03-16 12:29:55 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-03-16 12:44:49 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-03-16 12:59:44 | Compressor run ignoring free cooling Opportunity of 3.97 kWh
WLLS1 | RTU1 | 2024-03-16 14:45:01 | Compressor run ignoring free cooling Opportunity of 9.32 kWh
WLLS1 | RTU1 | 2024-03-16 17:29:58 | Compressor run ignoring free cooling Opportunity of 4.82 kWh
WLLS1 | RTU1 | 2024-03-16 17:44:53 | Compressor run ignoring free cooling Opportunity of 4.84 kWh
WLLS1 | RTU1 | 2024-03-16 17:59:48 | Compressor run ignoring free cooling Opportunity of 5.00 kWh
WLLS1 | RTU1 | 2024-03-16 19:59:56 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-03-16 20:14:53 | Compressor run ignoring free cooling Opportunity of 4.84 kWh
WLLS1 | RTU1 | 2024-03-16 20:29:48 | Compressor run ignoring free cooling Opportunity of 5.11 kWh
WLLS1 | RTU1 | 2024-03-16 22:30:01 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-03-16 22:44:56 | Compressor run ignoring free cooling Opportunity of 4.89 kWh
WLLS1 | RTU1 | 2024-03-16 22:59:51 | Compressor run ignoring free cooling Opportunity of 4.60 kWh
WLLS1 | RTU1 | 2024-03-16 23:59:59 | Compressor run ignoring free cooling Opportunity of 4.60 kWh
WLLS1 | RTU1 | 2024-03-17 02:14:59 | Compressor run ignoring free cooling Opportunity of 4.28 kWh
WLLS1 | RTU1 | 2024-03-17 02:29:54 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-03-17 02:44:49 | Compressor run ignoring free cooling Opportunity of 9.46 kWh
WLLS1 | RTU1 | 2024-03-17 06:44:58 | Compressor run ignoring free cooling Opportunity of 4.82 kWh
WLLS1 | RTU1 | 2024-03-17 06:59:54 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-03-17 09:44:49 | Compressor run ignoring free cooling Opportunity of 4.68 kWh
WLLS1 | RTU1 | 2024-03-17 11:44:58 | Compressor run ignoring free cooling Opportunity of 4.46 kWh
WLLS1 | RTU1 | 2024-03-17 11:59:52 | Compressor run ignoring free cooling Opportunity of 4.44 kWh
WLLS1 | RTU1 | 2024-03-17 12:14:49 | Compressor run ignoring free cooling Opportunity of 4.39 kWh
WLLS1 | RTU1 | 2024-03-17 14:14:58 | Compressor run ignoring free cooling Opportunity of 4.84 kWh
WLLS1 | RTU1 | 2024-03-17 14:29:54 | Compressor run ignoring free cooling Opportunity of 4.91 kWh
WLLS1 | RTU1 | 2024-03-17 14:44:49 | Compressor run ignoring free cooling Opportunity of 4.53 kWh
WLLS1 | RTU1 | 2024-03-17 17:14:47 | Compressor run ignoring free cooling Opportunity of 4.46 kWh
WLLS1 | RTU1 | 2024-03-17 18:59:59 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-03-17 19:14:56 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-03-17 19:29:51 | Compressor run ignoring free cooling Opportunity of 3.23 kWh
WLLS1 | RTU1 | 2024-03-17 21:15:00 | Compressor run ignoring free cooling Opportunity of 4.97 kWh
WLLS1 | RTU1 | 2024-03-17 21:29:56 | Compressor run ignoring free cooling Opportunity of 3.17 kWh
WLLS1 | RTU1 | 2024-03-17 21:44:52 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-03-18 00:30:01 | Compressor run ignoring free cooling Opportunity of 3.30 kWh
WLLS1 | RTU1 | 2024-03-18 00:44:59 | Compressor run ignoring free cooling Opportunity of 4.71 kWh
WLLS1 | RTU1 | 2024-03-18 00:59:53 | Compressor run ignoring free cooling Opportunity of 4.82 kWh
WLLS1 | RTU1 | 2024-03-18 01:14:48 | Compressor run ignoring free cooling Opportunity of 4.68 kWh
WLLS1 | RTU1 | 2024-03-18 03:14:57 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-03-18 03:29:53 | Compressor run ignoring free cooling Opportunity of 4.71 kWh
WLLS1 | RTU1 | 2024-03-18 03:44:51 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-03-18 03:59:48 | Compressor run ignoring free cooling Opportunity of 5.02 kWh
WLLS1 | RTU1 | 2024-03-18 05:14:56 | Compressor run ignoring free cooling Opportunity of 5.00 kWh
WLLS1 | RTU1 | 2024-03-18 05:29:50 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-03-18 07:29:56 | Compressor run ignoring free cooling Opportunity of 4.97 kWh
WLLS1 | RTU1 | 2024-03-19 14:59:59 | Compressor run ignoring free cooling Opportunity of 3.01 kWh
WLLS1 | RTU1 | 2024-03-19 15:14:56 | Compressor run ignoring free cooling Opportunity of 5.38 kWh
WLLS1 | RTU1 | 2024-03-19 15:29:53 | Compressor run ignoring free cooling Opportunity of 4.33 kWh
WLLS1 | RTU1 | 2024-03-19 15:44:50 | Compressor run ignoring free cooling Opportunity of 4.60 kWh
WLLS1 | RTU1 | 2024-03-19 15:59:48 | Compressor run ignoring free cooling Opportunity of 4.55 kWh
WLLS1 | RTU1 | 2024-03-19 16:14:45 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-03-19 16:29:43 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-03-19 19:29:58 | Compressor run ignoring free cooling Opportunity of 3.15 kWh
WLLS1 | RTU1 | 2024-03-19 19:44:54 | Compressor run ignoring free cooling Opportunity of 4.33 kWh
WLLS1 | RTU1 | 2024-03-19 19:59:52 | Compressor run ignoring free cooling Opportunity of 3.08 kWh
WLLS1 | RTU1 | 2024-03-19 20:14:50 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-03-19 20:29:46 | Compressor run ignoring free cooling Opportunity of 3.01 kWh
WLLS1 | RTU1 | 2024-03-19 20:44:44 | Compressor run ignoring free cooling Opportunity of 4.51 kWh
WLLS1 | RTU1 | 2024-03-20 14:15:01 | Compressor run ignoring free cooling Opportunity of 4.51 kWh
WLLS1 | RTU1 | 2024-03-20 14:29:57 | Compressor run ignoring free cooling Opportunity of 4.15 kWh
WLLS1 | RTU1 | 2024-03-20 14:44:54 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-03-20 14:59:50 | Compressor run ignoring free cooling Opportunity of 4.31 kWh
WLLS1 | RTU1 | 2024-03-20 15:14:46 | Compressor run ignoring free cooling Opportunity of 3.84 kWh
WLLS1 | RTU1 | 2024-03-20 15:29:44 | Compressor run ignoring free cooling Opportunity of 4.60 kWh
WLLS1 | RTU1 | 2024-03-20 18:15:01 | Compressor run ignoring free cooling Opportunity of 4.97 kWh
WLLS1 | RTU1 | 2024-03-20 18:29:59 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-03-20 18:44:58 | Compressor run ignoring free cooling Opportunity of 3.21 kWh
WLLS1 | RTU1 | 2024-03-20 18:59:54 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-03-20 19:14:51 | Compressor run ignoring free cooling Opportunity of 3.15 kWh
WLLS1 | RTU1 | 2024-03-20 19:29:48 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-03-20 19:44:45 | Compressor run ignoring free cooling Opportunity of 3.21 kWh
WLLS1 | RTU1 | 2024-03-21 11:30:01 | Compressor run ignoring free cooling Opportunity of 3.06 kWh
WLLS1 | RTU1 | 2024-03-21 11:44:59 | Compressor run ignoring free cooling Opportunity of 3.55 kWh
WLLS1 | RTU1 | 2024-03-21 11:59:57 | Compressor run ignoring free cooling Opportunity of 4.39 kWh
WLLS1 | RTU1 | 2024-03-21 12:14:55 | Compressor run ignoring free cooling Opportunity of 3.01 kWh
WLLS1 | RTU1 | 2024-03-21 12:29:52 | Compressor run ignoring free cooling Opportunity of 4.37 kWh
WLLS1 | RTU1 | 2024-03-21 12:44:48 | Compressor run ignoring free cooling Opportunity of 3.08 kWh
WLLS1 | RTU1 | 2024-03-21 12:59:45 | Compressor run ignoring free cooling Opportunity of 4.57 kWh
WLLS1 | RTU1 | 2024-03-21 15:45:01 | Compressor run ignoring free cooling Opportunity of 3.68 kWh
WLLS1 | RTU1 | 2024-03-21 15:59:59 | Compressor run ignoring free cooling Opportunity of 3.08 kWh
WLLS1 | RTU1 | 2024-03-21 16:14:55 | Compressor run ignoring free cooling Opportunity of 4.46 kWh
WLLS1 | RTU1 | 2024-03-21 16:29:51 | Compressor run ignoring free cooling Opportunity of 3.23 kWh
WLLS1 | RTU1 | 2024-03-21 16:44:48 | Compressor run ignoring free cooling Opportunity of 4.39 kWh
WLLS1 | RTU1 | 2024-03-21 16:59:45 | Compressor run ignoring free cooling Opportunity of 3.23 kWh
WLLS1 | RTU1 | 2024-03-21 19:44:58 | Compressor run ignoring free cooling Opportunity of 5.00 kWh
WLLS1 | RTU1 | 2024-03-21 19:59:57 | Compressor run ignoring free cooling Opportunity of 2.99 kWh
WLLS1 | RTU1 | 2024-03-21 20:14:55 | Compressor run ignoring free cooling Opportunity of 3.06 kWh
WLLS1 | RTU1 | 2024-03-21 20:29:51 | Compressor run ignoring free cooling Opportunity of 3.08 kWh
WLLS1 | RTU1 | 2024-03-21 20:44:47 | Compressor run ignoring free cooling Opportunity of 3.15 kWh
WLLS1 | RTU1 | 2024-03-21 20:59:46 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-03-22 11:59:53 | Compressor run ignoring free cooling Opportunity of 3.15 kWh
WLLS1 | RTU1 | 2024-03-22 12:14:50 | Compressor run ignoring free cooling Opportunity of 4.44 kWh
WLLS1 | RTU1 | 2024-03-22 12:29:47 | Compressor run ignoring free cooling Opportunity of 3.01 kWh
WLLS1 | RTU1 | 2024-03-22 12:44:46 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-03-22 15:45:01 | Compressor run ignoring free cooling Opportunity of 4.80 kWh
WLLS1 | RTU1 | 2024-03-22 15:59:57 | Compressor run ignoring free cooling Opportunity of 4.91 kWh
WLLS1 | RTU1 | 2024-03-22 16:14:55 | Compressor run ignoring free cooling Opportunity of 5.06 kWh
WLLS1 | RTU1 | 2024-03-22 16:29:52 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-03-22 16:44:48 | Compressor run ignoring free cooling Opportunity of 4.60 kWh
WLLS1 | RTU1 | 2024-03-22 16:59:46 | Compressor run ignoring free cooling Opportunity of 4.60 kWh
WLLS1 | RTU1 | 2024-03-22 17:14:45 | Compressor run ignoring free cooling Opportunity of 4.22 kWh
WLLS1 | RTU1 | 2024-03-22 19:30:01 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-03-22 19:44:57 | Compressor run ignoring free cooling Opportunity of 4.89 kWh
WLLS1 | RTU1 | 2024-03-22 19:59:55 | Compressor run ignoring free cooling Opportunity of 4.91 kWh
WLLS1 | RTU1 | 2024-03-22 20:14:53 | Compressor run ignoring free cooling Opportunity of 5.26 kWh
WLLS1 | RTU1 | 2024-03-22 20:29:51 | Compressor run ignoring free cooling Opportunity of 5.31 kWh
WLLS1 | RTU1 | 2024-03-22 20:44:48 | Compressor run ignoring free cooling Opportunity of 4.80 kWh
WLLS1 | RTU1 | 2024-03-22 20:59:45 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-03-23 00:14:50 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU1 | 2024-03-23 00:29:47 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-03-23 03:15:00 | Compressor run ignoring free cooling Opportunity of 5.20 kWh
WLLS1 | RTU1 | 2024-03-23 09:59:55 | Compressor run ignoring free cooling Opportunity of 4.71 kWh
WLLS1 | RTU1 | 2024-03-23 10:14:51 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-03-23 10:29:48 | Compressor run ignoring free cooling Opportunity of 4.84 kWh
WLLS1 | RTU1 | 2024-03-23 13:00:01 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-03-23 13:44:52 | Compressor run ignoring free cooling Opportunity of 5.06 kWh
WLLS1 | RTU1 | 2024-03-23 13:59:49 | Compressor run ignoring free cooling Opportunity of 4.91 kWh
WLLS1 | RTU1 | 2024-03-23 14:14:46 | Compressor run ignoring free cooling Opportunity of 4.62 kWh
WLLS1 | RTU1 | 2024-03-23 14:29:45 | Compressor run ignoring free cooling Opportunity of 4.82 kWh
WLLS1 | RTU1 | 2024-03-23 14:44:43 | Compressor run ignoring free cooling Opportunity of 4.71 kWh
WLLS1 | RTU1 | 2024-03-23 17:29:59 | Compressor run ignoring free cooling Opportunity of 4.64 kWh
WLLS1 | RTU1 | 2024-03-23 17:44:57 | Compressor run ignoring free cooling Opportunity of 4.91 kWh
WLLS1 | RTU1 | 2024-03-23 17:59:54 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-03-23 18:14:50 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-03-23 18:29:50 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-03-23 18:44:48 | Compressor run ignoring free cooling Opportunity of 4.60 kWh
WLLS1 | RTU1 | 2024-03-23 18:59:45 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-03-23 21:45:02 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-03-23 22:00:00 | Compressor run ignoring free cooling Opportunity of 3.66 kWh
WLLS1 | RTU1 | 2024-03-23 22:14:59 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-03-23 22:29:56 | Compressor run ignoring free cooling Opportunity of 4.91 kWh
WLLS1 | RTU1 | 2024-03-23 22:44:52 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-03-23 22:59:49 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-03-23 23:14:45 | Compressor run ignoring free cooling Opportunity of 5.09 kWh
WLLS1 | RTU1 | 2024-03-25 16:00:00 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-03-25 16:14:57 | Compressor run ignoring free cooling Opportunity of 4.51 kWh
WLLS1 | RTU1 | 2024-03-25 16:29:53 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-03-25 16:44:49 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-03-25 16:59:46 | Compressor run ignoring free cooling Opportunity of 3.15 kWh
WLLS1 | RTU1 | 2024-03-27 00:59:50 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-03-30 19:14:54 | Compressor run ignoring free cooling Opportunity of 3.21 kWh
WLLS1 | RTU1 | 2024-03-30 19:29:57 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-03-30 22:29:42 | Compressor run ignoring free cooling Opportunity of 3.10 kWh
WLLS1 | RTU1 | 2024-03-30 23:14:50 | Compressor run ignoring free cooling Opportunity of 3.23 kWh
WLLS1 | RTU1 | 2024-03-31 21:29:43 | Compressor run ignoring free cooling Opportunity of 4.84 kWh
WLLS1 | RTU1 | 2024-03-31 21:44:46 | Compressor run ignoring free cooling Opportunity of 4.64 kWh
WLLS1 | RTU1 | 2024-03-31 21:59:51 | Compressor run ignoring free cooling Opportunity of 4.60 kWh
WLLS1 | RTU1 | 2024-03-31 22:14:55 | Compressor run ignoring free cooling Opportunity of 4.62 kWh
WLLS1 | RTU1 | 2024-03-31 23:44:53 | Compressor run ignoring free cooling Opportunity of 3.46 kWh
WLLS1 | RTU1 | 2024-04-01 00:44:42 | Compressor run ignoring free cooling Opportunity of 4.82 kWh
WLLS1 | RTU1 | 2024-04-01 00:59:47 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-04-01 01:14:50 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-04-01 01:29:52 | Compressor run ignoring free cooling Opportunity of 3.44 kWh
WLLS1 | RTU1 | 2024-04-01 04:14:42 | Compressor run ignoring free cooling Opportunity of 4.68 kWh
WLLS1 | RTU1 | 2024-04-01 04:29:45 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-04-01 04:44:48 | Compressor run ignoring free cooling Opportunity of 3.26 kWh
WLLS1 | RTU1 | 2024-04-01 05:59:42 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-04-01 06:14:45 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-04-01 06:29:48 | Compressor run ignoring free cooling Opportunity of 5.11 kWh
WLLS1 | RTU1 | 2024-04-01 06:44:52 | Compressor run ignoring free cooling Opportunity of 4.62 kWh
WLLS1 | RTU1 | 2024-04-01 06:59:55 | Compressor run ignoring free cooling Opportunity of 5.06 kWh
WLLS1 | RTU1 | 2024-04-01 07:14:58 | Compressor run ignoring free cooling Opportunity of 5.11 kWh
WLLS1 | RTU1 | 2024-04-01 09:29:40 | Compressor run ignoring free cooling Opportunity of 4.66 kWh
WLLS1 | RTU1 | 2024-04-01 09:44:43 | Compressor run ignoring free cooling Opportunity of 9.95 kWh
WLLS1 | RTU1 | 2024-04-01 09:59:45 | Compressor run ignoring free cooling Opportunity of 10.42 kWh
WLLS1 | RTU1 | 2024-04-01 10:14:48 | Compressor run ignoring free cooling Opportunity of 10.19 kWh
WLLS1 | RTU1 | 2024-04-01 10:29:53 | Compressor run ignoring free cooling Opportunity of 10.44 kWh
WLLS1 | RTU1 | 2024-04-01 10:44:56 | Compressor run ignoring free cooling Opportunity of 10.53 kWh
WLLS1 | RTU1 | 2024-04-01 20:44:50 | Compressor run ignoring free cooling Opportunity of 4.71 kWh
WLLS1 | RTU1 | 2024-04-01 20:59:54 | Compressor run ignoring free cooling Opportunity of 8.19 kWh
WLLS1 | RTU1 | 2024-04-01 21:14:57 | Compressor run ignoring free cooling Opportunity of 8.41 kWh
WLLS1 | RTU1 | 2024-04-01 23:14:41 | Compressor run ignoring free cooling Opportunity of 10.28 kWh
WLLS1 | RTU1 | 2024-04-02 00:14:51 | Compressor run ignoring free cooling Opportunity of 4.66 kWh
WLLS1 | RTU1 | 2024-04-02 00:29:53 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-04-02 00:44:57 | Compressor run ignoring free cooling Opportunity of 5.24 kWh
WLLS1 | RTU1 | 2024-04-02 02:44:42 | Compressor run ignoring free cooling Opportunity of 5.31 kWh
WLLS1 | RTU1 | 2024-04-02 02:59:44 | Compressor run ignoring free cooling Opportunity of 5.15 kWh
WLLS1 | RTU1 | 2024-04-02 03:14:48 | Compressor run ignoring free cooling Opportunity of 4.62 kWh
WLLS1 | RTU1 | 2024-04-02 03:29:51 | Compressor run ignoring free cooling Opportunity of 9.79 kWh
WLLS1 | RTU1 | 2024-04-02 03:44:54 | Compressor run ignoring free cooling Opportunity of 9.90 kWh
WLLS1 | RTU1 | 2024-04-02 03:59:56 | Compressor run ignoring free cooling Opportunity of 5.06 kWh
WLLS1 | RTU1 | 2024-04-02 05:14:50 | Compressor run ignoring free cooling Opportunity of 10.02 kWh
WLLS1 | RTU1 | 2024-04-02 05:29:52 | Compressor run ignoring free cooling Opportunity of 9.90 kWh
WLLS1 | RTU1 | 2024-04-02 05:44:57 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-04-02 08:14:43 | Compressor run ignoring free cooling Opportunity of 10.48 kWh
WLLS1 | RTU1 | 2024-04-02 08:29:46 | Compressor run ignoring free cooling Opportunity of 10.75 kWh
WLLS1 | RTU1 | 2024-04-02 08:44:50 | Compressor run ignoring free cooling Opportunity of 10.71 kWh
WLLS1 | RTU1 | 2024-04-02 08:59:55 | Compressor run ignoring free cooling Opportunity of 10.86 kWh
WLLS1 | RTU1 | 2024-04-02 09:14:57 | Compressor run ignoring free cooling Opportunity of 10.80 kWh
WLLS1 | RTU1 | 2024-04-02 22:14:51 | Compressor run ignoring free cooling Opportunity of 10.10 kWh
WLLS1 | RTU1 | 2024-04-02 22:29:54 | Compressor run ignoring free cooling Opportunity of 10.42 kWh
WLLS1 | RTU1 | 2024-04-02 22:44:57 | Compressor run ignoring free cooling Opportunity of 10.39 kWh
WLLS1 | RTU1 | 2024-04-02 23:44:46 | Compressor run ignoring free cooling Opportunity of 10.48 kWh
WLLS1 | RTU1 | 2024-04-03 01:14:42 | Compressor run ignoring free cooling Opportunity of 10.82 kWh
WLLS1 | RTU1 | 2024-04-03 01:29:44 | Compressor run ignoring free cooling Opportunity of 10.68 kWh
WLLS1 | RTU1 | 2024-04-03 01:44:47 | Compressor run ignoring free cooling Opportunity of 9.21 kWh
WLLS1 | RTU1 | 2024-04-03 01:59:54 | Compressor run ignoring free cooling Opportunity of 10.46 kWh
WLLS1 | RTU1 | 2024-04-03 02:14:58 | Compressor run ignoring free cooling Opportunity of 10.48 kWh
WLLS1 | RTU1 | 2024-04-03 04:14:40 | Compressor run ignoring free cooling Opportunity of 10.71 kWh
WLLS1 | RTU1 | 2024-04-03 04:29:45 | Compressor run ignoring free cooling Opportunity of 9.79 kWh
WLLS1 | RTU1 | 2024-04-03 04:44:49 | Compressor run ignoring free cooling Opportunity of 9.46 kWh
WLLS1 | RTU1 | 2024-04-03 06:14:42 | Compressor run ignoring free cooling Opportunity of 10.46 kWh
WLLS1 | RTU1 | 2024-04-03 06:29:44 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-04-03 06:44:47 | Compressor run ignoring free cooling Opportunity of 10.22 kWh
WLLS1 | RTU1 | 2024-04-03 06:59:50 | Compressor run ignoring free cooling Opportunity of 10.10 kWh
WLLS1 | RTU1 | 2024-04-03 07:14:54 | Compressor run ignoring free cooling Opportunity of 10.42 kWh
WLLS1 | RTU1 | 2024-04-03 07:29:56 | Compressor run ignoring free cooling Opportunity of 10.53 kWh
WLLS1 | RTU1 | 2024-04-03 08:14:40 | Compressor run ignoring free cooling Opportunity of 10.33 kWh
WLLS1 | RTU1 | 2024-04-04 10:29:55 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-04-04 10:44:58 | Compressor run ignoring free cooling Opportunity of 3.08 kWh
WLLS1 | RTU1 | 2024-04-04 17:44:54 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-04-04 20:29:42 | Compressor run ignoring free cooling Opportunity of 3.08 kWh
WLLS1 | RTU1 | 2024-04-05 15:14:40 | Compressor run ignoring free cooling Opportunity of 3.17 kWh
WLLS1 | RTU1 | 2024-04-05 15:29:43 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-04-05 15:44:45 | Compressor run ignoring free cooling Opportunity of 3.10 kWh
WLLS1 | RTU1 | 2024-04-05 15:59:49 | Compressor run ignoring free cooling Opportunity of 3.17 kWh
WLLS1 | RTU1 | 2024-04-05 16:14:52 | Compressor run ignoring free cooling Opportunity of 3.99 kWh
WLLS1 | RTU1 | 2024-04-05 18:29:42 | Compressor run ignoring free cooling Opportunity of 3.17 kWh
WLLS1 | RTU1 | 2024-04-05 18:44:44 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-04-05 18:59:47 | Compressor run ignoring free cooling Opportunity of 3.15 kWh
WLLS1 | RTU1 | 2024-04-07 17:44:41 | Compressor run ignoring free cooling Opportunity of 3.10 kWh
WLLS1 | RTU1 | 2024-04-07 17:59:44 | Compressor run ignoring free cooling Opportunity of 3.15 kWh
WLLS1 | RTU1 | 2024-04-07 18:14:47 | Compressor run ignoring free cooling Opportunity of 3.15 kWh
WLLS1 | RTU1 | 2024-04-07 18:29:50 | Compressor run ignoring free cooling Opportunity of 3.17 kWh
WLLS1 | RTU1 | 2024-04-07 18:44:53 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-04-07 18:59:55 | Compressor run ignoring free cooling Opportunity of 3.17 kWh
WLLS1 | RTU1 | 2024-04-07 19:14:58 | Compressor run ignoring free cooling Opportunity of 3.66 kWh
WLLS1 | RTU1 | 2024-04-19 09:59:49 | Compressor run ignoring free cooling Opportunity of 10.77 kWh
WLLS1 | RTU1 | 2024-04-19 10:59:42 | Compressor run ignoring free cooling Opportunity of 8.43 kWh
WLLS1 | RTU1 | 2024-04-19 11:14:51 | Compressor run ignoring free cooling Opportunity of 10.71 kWh
WLLS1 | RTU1 | 2024-04-19 19:44:41 | Compressor run ignoring free cooling Opportunity of 8.52 kWh
WLLS1 | RTU1 | 2024-04-19 19:59:51 | Compressor run ignoring free cooling Opportunity of 10.39 kWh
WLLS1 | RTU1 | 2024-04-19 20:59:41 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-04-19 21:14:50 | Compressor run ignoring free cooling Opportunity of 8.77 kWh
WLLS1 | RTU1 | 2024-04-19 22:29:47 | Compressor run ignoring free cooling Opportunity of 10.62 kWh
WLLS1 | RTU1 | 2024-04-20 00:14:49 | Compressor run ignoring free cooling Opportunity of 10.80 kWh
WLLS1 | RTU1 | 2024-04-20 01:14:43 | Compressor run ignoring free cooling Opportunity of 9.48 kWh
WLLS1 | RTU1 | 2024-04-20 01:29:50 | Compressor run ignoring free cooling Opportunity of 10.82 kWh
WLLS1 | RTU1 | 2024-04-20 02:29:42 | Compressor run ignoring free cooling Opportunity of 10.73 kWh
WLLS1 | RTU1 | 2024-04-20 02:44:50 | Compressor run ignoring free cooling Opportunity of 10.19 kWh
WLLS1 | RTU1 | 2024-04-20 03:59:48 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-04-20 05:44:45 | Compressor run ignoring free cooling Opportunity of 8.74 kWh
WLLS1 | RTU1 | 2024-04-20 06:59:48 | Compressor run ignoring free cooling Opportunity of 10.19 kWh
WLLS1 | RTU1 | 2024-04-20 08:14:45 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-04-20 09:29:47 | Compressor run ignoring free cooling Opportunity of 8.72 kWh
WLLS1 | RTU1 | 2024-04-20 10:44:47 | Compressor run ignoring free cooling Opportunity of 10.46 kWh
WLLS1 | RTU1 | 2024-04-20 20:29:44 | Compressor run ignoring free cooling Opportunity of 10.82 kWh
WLLS1 | RTU1 | 2024-04-20 21:44:44 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-04-20 22:59:45 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-04-20 23:44:46 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-04-21 00:29:50 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-04-21 01:29:40 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-04-21 02:44:41 | Compressor run ignoring free cooling Opportunity of 5.00 kWh
WLLS1 | RTU1 | 2024-04-21 02:59:50 | Compressor run ignoring free cooling Opportunity of 5.15 kWh
WLLS1 | RTU1 | 2024-04-21 04:14:49 | Compressor run ignoring free cooling Opportunity of 3.75 kWh
WLLS1 | RTU1 | 2024-04-21 05:59:43 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-04-21 06:14:52 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-04-21 07:14:43 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-04-21 08:29:41 | Compressor run ignoring free cooling Opportunity of 5.11 kWh
WLLS1 | RTU1 | 2024-04-21 08:44:50 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-04-21 09:44:41 | Compressor run ignoring free cooling Opportunity of 4.71 kWh
WLLS1 | RTU1 | 2024-04-21 10:59:41 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-04-21 11:14:52 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-04-21 12:14:43 | Compressor run ignoring free cooling Opportunity of 4.57 kWh
WLLS1 | RTU1 | 2024-04-21 13:29:40 | Compressor run ignoring free cooling Opportunity of 4.57 kWh
WLLS1 | RTU1 | 2024-04-21 13:44:49 | Compressor run ignoring free cooling Opportunity of 4.62 kWh
WLLS1 | RTU1 | 2024-04-21 14:59:46 | Compressor run ignoring free cooling Opportunity of 5.18 kWh
WLLS1 | RTU1 | 2024-04-21 16:14:46 | Compressor run ignoring free cooling Opportunity of 4.84 kWh
WLLS1 | RTU1 | 2024-04-21 17:29:49 | Compressor run ignoring free cooling Opportunity of 4.62 kWh
WLLS1 | RTU1 | 2024-04-21 18:44:50 | Compressor run ignoring free cooling Opportunity of 4.71 kWh
WLLS1 | RTU1 | 2024-04-21 19:44:40 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-04-21 19:59:51 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU1 | 2024-04-21 20:59:43 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-04-21 21:14:51 | Compressor run ignoring free cooling Opportunity of 4.57 kWh
WLLS1 | RTU1 | 2024-04-21 22:14:43 | Compressor run ignoring free cooling Opportunity of 4.57 kWh
WLLS1 | RTU1 | 2024-04-22 11:14:41 | Compressor run ignoring free cooling Opportunity of 4.68 kWh
WLLS1 | RTU1 | 2024-04-22 11:29:50 | Compressor run ignoring free cooling Opportunity of 4.51 kWh
WLLS1 | RTU1 | 2024-04-22 17:29:45 | Compressor run ignoring free cooling Opportunity of 3.17 kWh
WLLS1 | RTU1 | 2024-04-22 18:44:46 | Compressor run ignoring free cooling Opportunity of 4.44 kWh
WLLS1 | RTU1 | 2024-04-22 19:59:47 | Compressor run ignoring free cooling Opportunity of 3.10 kWh
WLLS1 | RTU1 | 2024-04-23 17:59:42 | Compressor run ignoring free cooling Opportunity of 3.19 kWh
WLLS1 | RTU1 | 2024-04-23 18:14:52 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-04-23 19:14:41 | Compressor run ignoring free cooling Opportunity of 3.12 kWh
WLLS1 | RTU1 | 2024-04-23 19:29:50 | Compressor run ignoring free cooling Opportunity of 4.89 kWh
WLLS1 | RTU1 | 2024-04-23 20:44:48 | Compressor run ignoring free cooling Opportunity of 3.19 kWh
WLLS1 | RTU1 | 2024-04-23 21:59:45 | Compressor run ignoring free cooling Opportunity of 3.75 kWh
WLLS1 | RTU1 | 2024-04-23 23:14:46 | Compressor run ignoring free cooling Opportunity of 3.17 kWh
WLLS1 | RTU1 | 2024-04-23 23:30:02 | Compressor run ignoring free cooling Opportunity of 3.15 kWh
WLLS1 | RTU1 | 2024-04-23 23:44:47 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU1 | 2024-04-24 08:29:43 | Compressor run ignoring free cooling Opportunity of 3.17 kWh
WLLS1 | RTU1 | 2024-04-24 09:29:39 | Compressor run ignoring free cooling Opportunity of 5.29 kWh
WLLS1 | RTU1 | 2024-04-24 09:44:48 | Compressor run ignoring free cooling Opportunity of 5.09 kWh
WLLS1 | RTU1 | 2024-04-24 13:29:43 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-04-24 14:44:42 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU1 | 2024-04-24 14:59:51 | Compressor run ignoring free cooling Opportunity of 5.26 kWh
WLLS1 | RTU1 | 2024-04-24 16:14:49 | Compressor run ignoring free cooling Opportunity of 10.97 kWh
WLLS1 | RTU1 | 2024-04-24 17:14:42 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-04-24 18:29:41 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-04-24 18:44:50 | Compressor run ignoring free cooling Opportunity of 4.71 kWh
WLLS1 | RTU1 | 2024-04-24 19:44:41 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-04-24 20:59:45 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-04-24 22:14:44 | Compressor run ignoring free cooling Opportunity of 5.06 kWh
WLLS1 | RTU1 | 2024-04-25 00:44:41 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-04-25 00:59:50 | Compressor run ignoring free cooling Opportunity of 5.15 kWh
WLLS1 | RTU1 | 2024-04-25 11:14:40 | Compressor run ignoring free cooling Opportunity of 10.24 kWh
WLLS1 | RTU1 | 2024-04-25 11:29:50 | Compressor run ignoring free cooling Opportunity of 8.52 kWh
WLLS1 | RTU1 | 2024-04-25 18:59:46 | Compressor run ignoring free cooling Opportunity of 4.97 kWh
WLLS1 | RTU1 | 2024-04-25 20:14:45 | Compressor run ignoring free cooling Opportunity of 9.77 kWh
WLLS1 | RTU1 | 2024-04-25 21:29:44 | Compressor run ignoring free cooling Opportunity of 9.95 kWh
WLLS1 | RTU1 | 2024-04-25 22:44:42 | Compressor run ignoring free cooling Opportunity of 5.29 kWh
WLLS1 | RTU1 | 2024-04-25 22:59:51 | Compressor run ignoring free cooling Opportunity of 3.37 kWh
WLLS1 | RTU1 | 2024-04-26 00:14:41 | Compressor run ignoring free cooling Opportunity of 4.46 kWh
WLLS1 | RTU1 | 2024-04-26 00:29:51 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-04-26 01:29:41 | Compressor run ignoring free cooling Opportunity of 5.22 kWh
WLLS1 | RTU1 | 2024-04-26 01:44:50 | Compressor run ignoring free cooling Opportunity of 4.17 kWh
WLLS1 | RTU1 | 2024-04-26 02:44:41 | Compressor run ignoring free cooling Opportunity of 5.02 kWh
WLLS1 | RTU1 | 2024-04-26 02:59:49 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-04-26 03:59:41 | Compressor run ignoring free cooling Opportunity of 4.89 kWh
WLLS1 | RTU1 | 2024-04-26 04:14:51 | Compressor run ignoring free cooling Opportunity of 5.06 kWh
WLLS1 | RTU1 | 2024-04-26 09:29:41 | Compressor run ignoring free cooling Opportunity of 5.06 kWh
WLLS1 | RTU1 | 2024-04-26 09:44:50 | Compressor run ignoring free cooling Opportunity of 4.89 kWh
WLLS1 | RTU1 | 2024-04-26 10:44:42 | Compressor run ignoring free cooling Opportunity of 4.91 kWh
WLLS1 | RTU1 | 2024-04-26 10:59:49 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-04-26 12:14:48 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-04-26 13:29:49 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-04-26 19:29:44 | Compressor run ignoring free cooling Opportunity of 5.09 kWh
WLLS1 | RTU1 | 2024-04-26 20:44:43 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-04-26 20:59:51 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-04-26 21:59:44 | Compressor run ignoring free cooling Opportunity of 4.91 kWh
WLLS1 | RTU1 | 2024-04-26 23:14:44 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-04-27 00:44:46 | Compressor run ignoring free cooling Opportunity of 4.68 kWh
WLLS1 | RTU1 | 2024-04-27 01:59:48 | Compressor run ignoring free cooling Opportunity of 5.31 kWh
WLLS1 | RTU1 | 2024-04-27 03:14:45 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU1 | 2024-04-27 04:29:43 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-04-27 04:44:51 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-04-27 05:00:02 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-04-27 05:14:45 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU1 | 2024-04-27 06:44:53 | Compressor run ignoring free cooling Opportunity of 5.02 kWh
WLLS1 | RTU1 | 2024-04-27 07:44:43 | Compressor run ignoring free cooling Opportunity of 4.71 kWh
WLLS1 | RTU1 | 2024-04-27 08:59:44 | Compressor run ignoring free cooling Opportunity of 4.57 kWh
WLLS1 | RTU1 | 2024-04-27 10:14:48 | Compressor run ignoring free cooling Opportunity of 5.06 kWh
WLLS1 | RTU1 | 2024-04-27 11:29:47 | Compressor run ignoring free cooling Opportunity of 5.20 kWh
WLLS1 | RTU1 | 2024-04-27 19:59:45 | Compressor run ignoring free cooling Opportunity of 10.75 kWh
WLLS1 | RTU1 | 2024-04-27 21:14:44 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-04-27 22:29:43 | Compressor run ignoring free cooling Opportunity of 5.09 kWh
WLLS1 | RTU1 | 2024-04-28 00:14:48 | Compressor run ignoring free cooling Opportunity of 5.15 kWh
WLLS1 | RTU1 | 2024-04-28 01:29:46 | Compressor run ignoring free cooling Opportunity of 5.00 kWh
WLLS1 | RTU1 | 2024-04-28 02:44:46 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-04-28 03:59:49 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-04-28 05:59:52 | Compressor run ignoring free cooling Opportunity of 5.31 kWh
WLLS1 | RTU1 | 2024-04-28 07:14:50 | Compressor run ignoring free cooling Opportunity of 5.15 kWh
WLLS1 | RTU1 | 2024-04-28 08:14:43 | Compressor run ignoring free cooling Opportunity of 4.80 kWh
WLLS1 | RTU1 | 2024-04-28 08:29:52 | Compressor run ignoring free cooling Opportunity of 8.86 kWh
WLLS1 | RTU1 | 2024-04-28 09:29:41 | Compressor run ignoring free cooling Opportunity of 10.37 kWh
WLLS1 | RTU1 | 2024-04-28 09:44:50 | Compressor run ignoring free cooling Opportunity of 10.24 kWh
WLLS1 | RTU1 | 2024-04-28 19:44:51 | Compressor run ignoring free cooling Opportunity of 10.80 kWh
WLLS1 | RTU1 | 2024-04-28 20:44:45 | Compressor run ignoring free cooling Opportunity of 10.42 kWh
WLLS1 | RTU1 | 2024-04-28 21:59:48 | Compressor run ignoring free cooling Opportunity of 10.02 kWh
WLLS1 | RTU1 | 2024-04-28 22:59:49 | Compressor run ignoring free cooling Opportunity of 9.84 kWh
WLLS1 | RTU1 | 2024-04-29 00:14:40 | Compressor run ignoring free cooling Opportunity of 9.73 kWh
WLLS1 | RTU1 | 2024-04-29 00:29:51 | Compressor run ignoring free cooling Opportunity of 4.89 kWh
WLLS1 | RTU1 | 2024-04-29 01:29:41 | Compressor run ignoring free cooling Opportunity of 5.04 kWh
WLLS1 | RTU1 | 2024-04-29 02:44:44 | Compressor run ignoring free cooling Opportunity of 5.31 kWh
WLLS1 | RTU1 | 2024-04-29 03:59:44 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-04-29 05:59:48 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-04-29 07:14:47 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU1 | 2024-04-29 08:29:45 | Compressor run ignoring free cooling Opportunity of 10.51 kWh
WLLS1 | RTU1 | 2024-04-29 21:14:46 | Compressor run ignoring free cooling Opportunity of 4.80 kWh
WLLS1 | RTU1 | 2024-04-29 22:29:45 | Compressor run ignoring free cooling Opportunity of 4.89 kWh
WLLS1 | RTU1 | 2024-04-30 00:14:48 | Compressor run ignoring free cooling Opportunity of 9.06 kWh
WLLS1 | RTU1 | 2024-04-30 01:14:41 | Compressor run ignoring free cooling Opportunity of 10.62 kWh
WLLS1 | RTU1 | 2024-04-30 01:29:50 | Compressor run ignoring free cooling Opportunity of 10.68 kWh
WLLS1 | RTU1 | 2024-04-30 02:29:40 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-04-30 02:44:49 | Compressor run ignoring free cooling Opportunity of 8.68 kWh
WLLS1 | RTU1 | 2024-04-30 03:44:48 | Compressor run ignoring free cooling Opportunity of 8.70 kWh
WLLS1 | RTU1 | 2024-04-30 04:44:40 | Compressor run ignoring free cooling Opportunity of 9.95 kWh
WLLS1 | RTU1 | 2024-04-30 05:29:44 | Compressor run ignoring free cooling Opportunity of 4.62 kWh
WLLS1 | RTU1 | 2024-04-30 06:44:45 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-04-30 07:59:44 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-04-30 09:14:44 | Compressor run ignoring free cooling Opportunity of 10.84 kWh
WLLS1 | RTU1 | 2024-04-30 21:29:46 | Compressor run ignoring free cooling Opportunity of 10.39 kWh
WLLS1 | RTU1 | 2024-04-30 22:44:46 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-05-01 00:14:47 | Compressor run ignoring free cooling Opportunity of 10.48 kWh
WLLS1 | RTU1 | 2024-05-01 01:14:40 | Compressor run ignoring free cooling Opportunity of 8.65 kWh
WLLS1 | RTU1 | 2024-05-01 01:29:52 | Compressor run ignoring free cooling Opportunity of 10.53 kWh
WLLS1 | RTU1 | 2024-05-01 02:29:42 | Compressor run ignoring free cooling Opportunity of 10.71 kWh
WLLS1 | RTU1 | 2024-05-01 02:44:50 | Compressor run ignoring free cooling Opportunity of 8.59 kWh
WLLS1 | RTU1 | 2024-05-01 03:59:47 | Compressor run ignoring free cooling Opportunity of 10.55 kWh
WLLS1 | RTU1 | 2024-05-01 05:44:44 | Compressor run ignoring free cooling Opportunity of 10.95 kWh
WLLS1 | RTU1 | 2024-05-01 06:59:44 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-05-01 08:14:44 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-05-01 21:15:01 | Compressor run ignoring free cooling Opportunity of 9.77 kWh
WLLS1 | RTU1 | 2024-05-01 21:59:58 | Compressor run ignoring free cooling Opportunity of 10.24 kWh
WLLS1 | RTU1 | 2024-05-01 23:29:52 | Compressor run ignoring free cooling Opportunity of 10.53 kWh
WLLS1 | RTU1 | 2024-05-02 00:30:00 | Compressor run ignoring free cooling Opportunity of 8.92 kWh
WLLS1 | RTU1 | 2024-05-02 04:44:59 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-05-02 04:59:42 | Compressor run ignoring free cooling Opportunity of 10.95 kWh
WLLS1 | RTU1 | 2024-05-02 05:45:01 | Compressor run ignoring free cooling Opportunity of 9.23 kWh
WLLS1 | RTU1 | 2024-05-02 06:30:00 | Compressor run ignoring free cooling Opportunity of 10.28 kWh
WLLS1 | RTU1 | 2024-05-02 21:15:01 | Compressor run ignoring free cooling Opportunity of 5.09 kWh
WLLS1 | RTU1 | 2024-05-02 21:59:58 | Compressor run ignoring free cooling Opportunity of 9.90 kWh
WLLS1 | RTU1 | 2024-05-02 23:29:53 | Compressor run ignoring free cooling Opportunity of 10.46 kWh
WLLS1 | RTU1 | 2024-05-02 23:45:00 | Compressor run ignoring free cooling Opportunity of 10.39 kWh
WLLS1 | RTU1 | 2024-05-03 00:44:57 | Compressor run ignoring free cooling Opportunity of 10.68 kWh
WLLS1 | RTU1 | 2024-05-03 04:14:59 | Compressor run ignoring free cooling Opportunity of 10.31 kWh
WLLS1 | RTU1 | 2024-05-03 05:59:58 | Compressor run ignoring free cooling Opportunity of 10.73 kWh
WLLS1 | RTU1 | 2024-05-04 04:29:58 | Compressor run ignoring free cooling Opportunity of 10.60 kWh
WLLS1 | RTU1 | 2024-05-04 06:14:57 | Compressor run ignoring free cooling Opportunity of 10.46 kWh
WLLS1 | RTU1 | 2024-05-04 09:45:00 | Compressor run ignoring free cooling Opportunity of 10.31 kWh
WLLS1 | RTU1 | 2024-05-04 22:30:01 | Compressor run ignoring free cooling Opportunity of 8.34 kWh
WLLS1 | RTU1 | 2024-05-04 23:14:58 | Compressor run ignoring free cooling Opportunity of 8.61 kWh
WLLS1 | RTU1 | 2024-05-04 23:29:40 | Compressor run ignoring free cooling Opportunity of 10.37 kWh
WLLS1 | RTU1 | 2024-05-05 03:14:59 | Compressor run ignoring free cooling Opportunity of 10.80 kWh
WLLS1 | RTU1 | 2024-05-05 05:44:59 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-05-05 19:14:58 | Compressor run ignoring free cooling Opportunity of 10.55 kWh
WLLS1 | RTU1 | 2024-05-05 22:44:59 | Compressor run ignoring free cooling Opportunity of 10.48 kWh
WLLS1 | RTU1 | 2024-05-05 23:59:45 | Compressor run ignoring free cooling Opportunity of 8.86 kWh
WLLS1 | RTU1 | 2024-05-06 00:45:01 | Compressor run ignoring free cooling Opportunity of 10.33 kWh
WLLS1 | RTU1 | 2024-05-06 08:15:00 | Compressor run ignoring free cooling Opportunity of 10.80 kWh
WLLS1 | RTU1 | 2024-05-06 19:29:40 | Compressor run ignoring free cooling Opportunity of 10.55 kWh
WLLS1 | RTU1 | 2024-05-06 19:44:51 | Compressor run ignoring free cooling Opportunity of 10.62 kWh
WLLS1 | RTU1 | 2024-05-06 20:44:42 | Compressor run ignoring free cooling Opportunity of 10.19 kWh
WLLS1 | RTU1 | 2024-05-06 20:59:51 | Compressor run ignoring free cooling Opportunity of 10.28 kWh
WLLS1 | RTU1 | 2024-05-06 22:14:52 | Compressor run ignoring free cooling Opportunity of 10.13 kWh
WLLS1 | RTU1 | 2024-05-06 23:14:42 | Compressor run ignoring free cooling Opportunity of 10.53 kWh
WLLS1 | RTU1 | 2024-05-06 23:59:42 | Compressor run ignoring free cooling Opportunity of 10.60 kWh
WLLS1 | RTU1 | 2024-05-07 00:59:41 | Compressor run ignoring free cooling Opportunity of 10.84 kWh
WLLS1 | RTU1 | 2024-05-07 02:14:43 | Compressor run ignoring free cooling Opportunity of 10.48 kWh
WLLS1 | RTU1 | 2024-05-07 03:29:45 | Compressor run ignoring free cooling Opportunity of 10.82 kWh
WLLS1 | RTU1 | 2024-05-07 04:44:45 | Compressor run ignoring free cooling Opportunity of 10.33 kWh
WLLS1 | RTU1 | 2024-05-07 05:29:46 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-05-07 06:44:47 | Compressor run ignoring free cooling Opportunity of 10.42 kWh
WLLS1 | RTU1 | 2024-05-07 07:59:47 | Compressor run ignoring free cooling Opportunity of 10.35 kWh
WLLS1 | RTU1 | 2024-05-07 09:14:47 | Compressor run ignoring free cooling Opportunity of 10.44 kWh
WLLS1 | RTU1 | 2024-05-07 22:00:00 | Compressor run ignoring free cooling Opportunity of 8.74 kWh
WLLS1 | RTU1 | 2024-05-07 23:29:54 | Compressor run ignoring free cooling Opportunity of 10.35 kWh
WLLS1 | RTU1 | 2024-05-07 23:45:00 | Compressor run ignoring free cooling Opportunity of 8.57 kWh
WLLS1 | RTU1 | 2024-05-08 02:45:00 | Compressor run ignoring free cooling Opportunity of 10.68 kWh
WLLS1 | RTU1 | 2024-05-08 03:29:58 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-05-08 04:59:53 | Compressor run ignoring free cooling Opportunity of 10.55 kWh
WLLS1 | RTU1 | 2024-05-08 05:14:58 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-05-08 22:29:45 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-05-09 00:29:47 | Compressor run ignoring free cooling Opportunity of 8.61 kWh
WLLS1 | RTU1 | 2024-05-09 01:44:44 | Compressor run ignoring free cooling Opportunity of 10.55 kWh
WLLS1 | RTU1 | 2024-05-09 02:59:42 | Compressor run ignoring free cooling Opportunity of 10.46 kWh
WLLS1 | RTU1 | 2024-05-09 03:14:51 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-05-09 04:29:44 | Compressor run ignoring free cooling Opportunity of 10.82 kWh
WLLS1 | RTU1 | 2024-05-09 04:44:53 | Compressor run ignoring free cooling Opportunity of 10.60 kWh
WLLS1 | RTU1 | 2024-05-09 05:00:01 | Compressor run ignoring free cooling Opportunity of 10.77 kWh
WLLS1 | RTU1 | 2024-05-09 05:14:43 | Compressor run ignoring free cooling Opportunity of 10.89 kWh
WLLS1 | RTU1 | 2024-05-09 05:29:52 | Compressor run ignoring free cooling Opportunity of 10.80 kWh
WLLS1 | RTU1 | 2024-05-09 06:44:44 | Compressor run ignoring free cooling Opportunity of 10.89 kWh
WLLS1 | RTU1 | 2024-05-10 00:14:42 | Compressor run ignoring free cooling Opportunity of 9.32 kWh
WLLS1 | RTU1 | 2024-05-10 00:29:41 | Compressor run ignoring free cooling Opportunity of 10.77 kWh
WLLS1 | RTU1 | 2024-05-10 19:44:58 | Compressor run ignoring free cooling Opportunity of 9.90 kWh
WLLS1 | RTU1 | 2024-05-10 19:59:50 | Compressor run ignoring free cooling Opportunity of 8.54 kWh
WLLS1 | RTU1 | 2024-05-10 21:29:55 | Compressor run ignoring free cooling Opportunity of 4.44 kWh
WLLS1 | RTU1 | 2024-05-10 21:44:48 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-05-10 23:00:00 | Compressor run ignoring free cooling Opportunity of 8.23 kWh
WLLS1 | RTU1 | 2024-05-10 23:14:52 | Compressor run ignoring free cooling Opportunity of 10.31 kWh
WLLS1 | RTU1 | 2024-05-10 23:29:44 | Compressor run ignoring free cooling Opportunity of 10.37 kWh
WLLS1 | RTU1 | 2024-05-10 23:45:00 | Compressor run ignoring free cooling Opportunity of 8.77 kWh
WLLS1 | RTU1 | 2024-05-10 23:59:53 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-05-11 00:14:55 | Compressor run ignoring free cooling Opportunity of 4.97 kWh
WLLS1 | RTU1 | 2024-05-11 00:29:48 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-05-11 01:59:55 | Compressor run ignoring free cooling Opportunity of 4.89 kWh
WLLS1 | RTU1 | 2024-05-11 02:14:48 | Compressor run ignoring free cooling Opportunity of 5.02 kWh
WLLS1 | RTU1 | 2024-05-11 03:29:58 | Compressor run ignoring free cooling Opportunity of 4.57 kWh
WLLS1 | RTU1 | 2024-05-11 03:44:52 | Compressor run ignoring free cooling Opportunity of 4.22 kWh
WLLS1 | RTU1 | 2024-05-11 05:59:56 | Compressor run ignoring free cooling Opportunity of 4.80 kWh
WLLS1 | RTU1 | 2024-05-11 06:14:48 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-05-11 07:44:53 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-05-11 09:14:58 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-05-11 09:29:50 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-05-11 10:59:56 | Compressor run ignoring free cooling Opportunity of 5.06 kWh
WLLS1 | RTU1 | 2024-05-11 11:14:48 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU1 | 2024-05-11 12:44:57 | Compressor run ignoring free cooling Opportunity of 5.00 kWh
WLLS1 | RTU1 | 2024-05-11 12:59:51 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU1 | 2024-05-11 14:29:54 | Compressor run ignoring free cooling Opportunity of 5.00 kWh
WLLS1 | RTU1 | 2024-05-11 14:44:48 | Compressor run ignoring free cooling Opportunity of 4.89 kWh
WLLS1 | RTU1 | 2024-05-11 19:29:58 | Compressor run ignoring free cooling Opportunity of 5.11 kWh
WLLS1 | RTU1 | 2024-05-11 19:44:52 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU1 | 2024-05-11 21:15:01 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-05-11 21:29:53 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-05-11 22:59:59 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-05-11 23:14:53 | Compressor run ignoring free cooling Opportunity of 4.31 kWh
WLLS1 | RTU1 | 2024-05-11 23:59:55 | Compressor run ignoring free cooling Opportunity of 5.22 kWh
WLLS1 | RTU1 | 2024-05-12 00:14:57 | Compressor run ignoring free cooling Opportunity of 4.82 kWh
WLLS1 | RTU1 | 2024-05-12 00:29:49 | Compressor run ignoring free cooling Opportunity of 5.26 kWh
WLLS1 | RTU1 | 2024-05-12 01:59:56 | Compressor run ignoring free cooling Opportunity of 5.11 kWh
WLLS1 | RTU1 | 2024-05-12 02:14:49 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-05-12 03:44:58 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-05-12 03:59:50 | Compressor run ignoring free cooling Opportunity of 4.71 kWh
WLLS1 | RTU1 | 2024-05-12 06:14:56 | Compressor run ignoring free cooling Opportunity of 5.22 kWh
WLLS1 | RTU1 | 2024-05-12 06:29:51 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-05-12 07:59:57 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-05-12 08:14:49 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-05-12 19:44:59 | Compressor run ignoring free cooling Opportunity of 4.97 kWh
WLLS1 | RTU1 | 2024-05-12 19:59:53 | Compressor run ignoring free cooling Opportunity of 3.28 kWh
WLLS1 | RTU1 | 2024-05-12 21:30:00 | Compressor run ignoring free cooling Opportunity of 5.15 kWh
WLLS1 | RTU1 | 2024-05-12 21:44:52 | Compressor run ignoring free cooling Opportunity of 3.28 kWh
WLLS1 | RTU1 | 2024-05-12 23:14:57 | Compressor run ignoring free cooling Opportunity of 4.91 kWh
WLLS1 | RTU1 | 2024-05-13 00:29:56 | Compressor run ignoring free cooling Opportunity of 4.57 kWh
WLLS1 | RTU1 | 2024-05-13 00:44:49 | Compressor run ignoring free cooling Opportunity of 5.11 kWh
WLLS1 | RTU1 | 2024-05-13 02:00:01 | Compressor run ignoring free cooling Opportunity of 4.66 kWh
WLLS1 | RTU1 | 2024-05-13 02:14:56 | Compressor run ignoring free cooling Opportunity of 4.64 kWh
WLLS1 | RTU1 | 2024-05-13 02:29:47 | Compressor run ignoring free cooling Opportunity of 4.80 kWh
WLLS1 | RTU1 | 2024-05-13 03:59:53 | Compressor run ignoring free cooling Opportunity of 3.39 kWh
WLLS1 | RTU1 | 2024-05-13 06:14:56 | Compressor run ignoring free cooling Opportunity of 4.60 kWh
WLLS1 | RTU1 | 2024-05-13 06:29:47 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-05-13 07:45:00 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU1 | 2024-05-13 07:59:53 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU1 | 2024-05-13 22:00:00 | Compressor run ignoring free cooling Opportunity of 8.21 kWh
WLLS1 | RTU1 | 2024-05-13 22:15:00 | Compressor run ignoring free cooling Opportunity of 4.80 kWh
WLLS1 | RTU1 | 2024-05-13 22:29:58 | Compressor run ignoring free cooling Opportunity of 4.91 kWh
WLLS1 | RTU1 | 2024-05-13 22:44:56 | Compressor run ignoring free cooling Opportunity of 5.11 kWh
WLLS1 | RTU1 | 2024-05-13 22:59:56 | Compressor run ignoring free cooling Opportunity of 4.97 kWh
WLLS1 | RTU1 | 2024-05-13 23:14:55 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-05-14 03:15:00 | Compressor run ignoring free cooling Opportunity of 5.00 kWh
WLLS1 | RTU1 | 2024-05-14 03:29:58 | Compressor run ignoring free cooling Opportunity of 10.86 kWh
WLLS1 | RTU1 | 2024-05-14 03:44:56 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-05-14 03:59:54 | Compressor run ignoring free cooling Opportunity of 9.03 kWh
WLLS1 | RTU1 | 2024-05-14 04:14:53 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-05-14 04:29:51 | Compressor run ignoring free cooling Opportunity of 6.38 kWh
WLLS1 | RTU1 | 2024-05-14 04:44:50 | Compressor run ignoring free cooling Opportunity of 10.73 kWh
WLLS1 | RTU1 | 2024-05-14 06:45:02 | Compressor run ignoring free cooling Opportunity of 11.06 kWh
WLLS1 | RTU1 | 2024-05-14 07:00:01 | Compressor run ignoring free cooling Opportunity of 8.81 kWh
WLLS1 | RTU1 | 2024-05-14 07:14:59 | Compressor run ignoring free cooling Opportunity of 11.02 kWh
WLLS1 | RTU1 | 2024-05-14 07:29:58 | Compressor run ignoring free cooling Opportunity of 10.75 kWh
WLLS1 | RTU1 | 2024-05-14 07:44:56 | Compressor run ignoring free cooling Opportunity of 11.00 kWh
WLLS1 | RTU1 | 2024-05-14 07:59:54 | Compressor run ignoring free cooling Opportunity of 11.00 kWh
WLLS1 | RTU1 | 2024-05-14 08:14:52 | Compressor run ignoring free cooling Opportunity of 8.61 kWh
WLLS1 | RTU1 | 2024-05-14 08:29:52 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-05-14 08:44:52 | Compressor run ignoring free cooling Opportunity of 10.82 kWh
WLLS1 | RTU1 | 2024-05-14 08:59:51 | Compressor run ignoring free cooling Opportunity of 8.50 kWh
WLLS1 | RTU1 | 2024-05-14 09:14:49 | Compressor run ignoring free cooling Opportunity of 10.71 kWh
WLLS1 | RTU1 | 2024-05-14 09:29:48 | Compressor run ignoring free cooling Opportunity of 10.84 kWh
WLLS1 | RTU1 | 2024-05-14 09:44:46 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-05-14 09:59:47 | Compressor run ignoring free cooling Opportunity of 11.04 kWh
WLLS1 | RTU1 | 2024-05-14 10:14:45 | Compressor run ignoring free cooling Opportunity of 10.84 kWh
WLLS1 | RTU1 | 2024-05-14 10:29:43 | Compressor run ignoring free cooling Opportunity of 10.97 kWh
WLLS1 | RTU1 | 2024-05-14 16:59:58 | Compressor run ignoring free cooling Opportunity of 10.86 kWh
WLLS1 | RTU1 | 2024-05-14 17:14:57 | Compressor run ignoring free cooling Opportunity of 10.82 kWh
WLLS1 | RTU1 | 2024-05-14 17:29:55 | Compressor run ignoring free cooling Opportunity of 10.86 kWh
WLLS1 | RTU1 | 2024-05-14 17:44:55 | Compressor run ignoring free cooling Opportunity of 10.86 kWh
WLLS1 | RTU1 | 2024-05-14 17:59:56 | Compressor run ignoring free cooling Opportunity of 10.95 kWh
WLLS1 | RTU1 | 2024-05-14 18:14:54 | Compressor run ignoring free cooling Opportunity of 10.93 kWh
WLLS1 | RTU1 | 2024-05-14 18:29:53 | Compressor run ignoring free cooling Opportunity of 10.84 kWh
WLLS1 | RTU1 | 2024-05-14 18:44:51 | Compressor run ignoring free cooling Opportunity of 10.13 kWh
WLLS1 | RTU1 | 2024-05-14 18:59:52 | Compressor run ignoring free cooling Opportunity of 10.53 kWh
WLLS1 | RTU1 | 2024-05-14 19:14:49 | Compressor run ignoring free cooling Opportunity of 10.82 kWh
WLLS1 | RTU1 | 2024-05-14 19:29:49 | Compressor run ignoring free cooling Opportunity of 10.24 kWh
WLLS1 | RTU1 | 2024-05-14 19:44:46 | Compressor run ignoring free cooling Opportunity of 10.26 kWh
WLLS1 | RTU1 | 2024-05-14 19:59:44 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-05-14 20:14:42 | Compressor run ignoring free cooling Opportunity of 10.71 kWh
WLLS1 | RTU1 | 2024-05-15 04:15:01 | Compressor run ignoring free cooling Opportunity of 9.08 kWh
WLLS1 | RTU1 | 2024-05-15 04:30:00 | Compressor run ignoring free cooling Opportunity of 10.93 kWh
WLLS1 | RTU1 | 2024-05-15 04:44:58 | Compressor run ignoring free cooling Opportunity of 10.02 kWh
WLLS1 | RTU1 | 2024-05-15 08:45:01 | Compressor run ignoring free cooling Opportunity of 10.77 kWh
WLLS1 | RTU1 | 2024-05-15 09:00:00 | Compressor run ignoring free cooling Opportunity of 10.62 kWh
WLLS1 | RTU1 | 2024-05-15 11:14:42 | Compressor run ignoring free cooling Opportunity of 10.46 kWh
WLLS1 | RTU1 | 2024-05-15 11:29:41 | Compressor run ignoring free cooling Opportunity of 10.60 kWh
WLLS1 | RTU1 | 2024-05-15 19:29:43 | Compressor run ignoring free cooling Opportunity of 10.28 kWh
WLLS1 | RTU1 | 2024-05-15 19:44:42 | Compressor run ignoring free cooling Opportunity of 9.97 kWh
WLLS1 | RTU1 | 2024-05-15 19:59:42 | Compressor run ignoring free cooling Opportunity of 10.28 kWh
WLLS1 | RTU1 | 2024-05-15 23:44:43 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-05-15 23:59:42 | Compressor run ignoring free cooling Opportunity of 10.82 kWh
WLLS1 | RTU1 | 2024-05-16 00:14:51 | Compressor run ignoring free cooling Opportunity of 10.73 kWh
WLLS1 | RTU1 | 2024-05-16 00:29:49 | Compressor run ignoring free cooling Opportunity of 10.71 kWh
WLLS1 | RTU1 | 2024-05-16 00:44:48 | Compressor run ignoring free cooling Opportunity of 10.82 kWh
WLLS1 | RTU1 | 2024-05-16 00:59:47 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-05-16 01:14:48 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-05-16 01:29:46 | Compressor run ignoring free cooling Opportunity of 10.77 kWh
WLLS1 | RTU1 | 2024-05-16 01:44:46 | Compressor run ignoring free cooling Opportunity of 10.91 kWh
WLLS1 | RTU1 | 2024-05-16 01:59:43 | Compressor run ignoring free cooling Opportunity of 9.41 kWh
WLLS1 | RTU1 | 2024-05-16 05:14:44 | Compressor run ignoring free cooling Opportunity of 10.75 kWh
WLLS1 | RTU1 | 2024-05-16 05:29:42 | Compressor run ignoring free cooling Opportunity of 8.70 kWh
WLLS1 | RTU1 | 2024-05-16 20:44:41 | Compressor run ignoring free cooling Opportunity of 8.88 kWh
WLLS1 | RTU1 | 2024-05-16 21:59:45 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-05-16 23:14:44 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-05-16 23:29:55 | Compressor run ignoring free cooling Opportunity of 10.97 kWh
WLLS1 | RTU1 | 2024-05-16 23:44:40 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-05-17 00:29:40 | Compressor run ignoring free cooling Opportunity of 10.71 kWh
WLLS1 | RTU1 | 2024-05-17 00:44:49 | Compressor run ignoring free cooling Opportunity of 9.64 kWh
WLLS1 | RTU1 | 2024-05-17 01:59:46 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-05-17 02:59:39 | Compressor run ignoring free cooling Opportunity of 10.80 kWh
WLLS1 | RTU1 | 2024-05-17 03:14:48 | Compressor run ignoring free cooling Opportunity of 10.62 kWh
WLLS1 | RTU1 | 2024-05-17 04:14:39 | Compressor run ignoring free cooling Opportunity of 10.48 kWh
WLLS1 | RTU1 | 2024-05-17 04:29:50 | Compressor run ignoring free cooling Opportunity of 10.51 kWh
WLLS1 | RTU1 | 2024-05-17 06:14:48 | Compressor run ignoring free cooling Opportunity of 10.73 kWh
WLLS1 | RTU1 | 2024-05-17 07:14:42 | Compressor run ignoring free cooling Opportunity of 10.86 kWh
WLLS1 | RTU1 | 2024-05-17 18:29:41 | Compressor run ignoring free cooling Opportunity of 10.39 kWh
WLLS1 | RTU1 | 2024-05-17 18:44:50 | Compressor run ignoring free cooling Opportunity of 10.42 kWh
WLLS1 | RTU1 | 2024-05-17 19:44:42 | Compressor run ignoring free cooling Opportunity of 10.44 kWh
WLLS1 | RTU1 | 2024-05-17 20:59:40 | Compressor run ignoring free cooling Opportunity of 10.60 kWh
WLLS1 | RTU1 | 2024-05-17 21:14:48 | Compressor run ignoring free cooling Opportunity of 10.26 kWh
WLLS1 | RTU1 | 2024-05-17 22:29:49 | Compressor run ignoring free cooling Opportunity of 10.51 kWh
WLLS1 | RTU1 | 2024-05-18 00:59:40 | Compressor run ignoring free cooling Opportunity of 9.39 kWh
WLLS1 | RTU1 | 2024-05-18 01:14:50 | Compressor run ignoring free cooling Opportunity of 10.62 kWh
WLLS1 | RTU1 | 2024-05-18 02:14:43 | Compressor run ignoring free cooling Opportunity of 10.93 kWh
WLLS1 | RTU1 | 2024-05-18 03:29:40 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-05-18 03:44:51 | Compressor run ignoring free cooling Opportunity of 10.93 kWh
WLLS1 | RTU1 | 2024-05-18 04:44:40 | Compressor run ignoring free cooling Opportunity of 10.84 kWh
WLLS1 | RTU1 | 2024-05-18 05:29:44 | Compressor run ignoring free cooling Opportunity of 11.06 kWh
WLLS1 | RTU1 | 2024-05-18 06:44:45 | Compressor run ignoring free cooling Opportunity of 10.91 kWh
WLLS1 | RTU1 | 2024-05-18 07:59:42 | Compressor run ignoring free cooling Opportunity of 10.82 kWh
WLLS1 | RTU1 | 2024-05-18 08:14:51 | Compressor run ignoring free cooling Opportunity of 10.71 kWh
WLLS1 | RTU1 | 2024-05-18 17:44:43 | Compressor run ignoring free cooling Opportunity of 10.31 kWh
WLLS1 | RTU1 | 2024-05-18 18:59:48 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-05-18 19:59:39 | Compressor run ignoring free cooling Opportunity of 10.39 kWh
WLLS1 | RTU1 | 2024-05-18 20:14:47 | Compressor run ignoring free cooling Opportunity of 10.60 kWh
WLLS1 | RTU1 | 2024-05-18 21:14:41 | Compressor run ignoring free cooling Opportunity of 10.62 kWh
WLLS1 | RTU1 | 2024-05-18 21:29:51 | Compressor run ignoring free cooling Opportunity of 10.51 kWh
WLLS1 | RTU1 | 2024-05-18 22:29:43 | Compressor run ignoring free cooling Opportunity of 10.46 kWh
WLLS1 | RTU1 | 2024-05-18 22:44:52 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-05-19 00:14:46 | Compressor run ignoring free cooling Opportunity of 8.54 kWh
WLLS1 | RTU1 | 2024-05-19 01:14:39 | Compressor run ignoring free cooling Opportunity of 10.48 kWh
WLLS1 | RTU1 | 2024-05-19 01:29:48 | Compressor run ignoring free cooling Opportunity of 10.68 kWh
WLLS1 | RTU1 | 2024-05-19 02:44:48 | Compressor run ignoring free cooling Opportunity of 10.77 kWh
WLLS1 | RTU1 | 2024-05-19 03:59:47 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-05-19 05:44:47 | Compressor run ignoring free cooling Opportunity of 5.24 kWh
WLLS1 | RTU1 | 2024-05-19 06:59:46 | Compressor run ignoring free cooling Opportunity of 10.24 kWh
WLLS1 | RTU1 | 2024-05-19 08:14:47 | Compressor run ignoring free cooling Opportunity of 8.59 kWh
WLLS1 | RTU1 | 2024-05-19 09:14:39 | Compressor run ignoring free cooling Opportunity of 10.55 kWh
WLLS1 | RTU1 | 2024-05-19 09:29:50 | Compressor run ignoring free cooling Opportunity of 10.53 kWh
WLLS1 | RTU1 | 2024-05-19 10:29:42 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-05-19 10:44:52 | Compressor run ignoring free cooling Opportunity of 10.51 kWh
WLLS1 | RTU1 | 2024-05-19 11:44:44 | Compressor run ignoring free cooling Opportunity of 10.62 kWh
WLLS1 | RTU1 | 2024-05-19 17:29:41 | Compressor run ignoring free cooling Opportunity of 10.33 kWh
WLLS1 | RTU1 | 2024-05-19 17:44:50 | Compressor run ignoring free cooling Opportunity of 10.68 kWh
WLLS1 | RTU1 | 2024-05-19 18:44:39 | Compressor run ignoring free cooling Opportunity of 10.80 kWh
WLLS1 | RTU1 | 2024-05-19 19:59:44 | Compressor run ignoring free cooling Opportunity of 10.53 kWh
WLLS1 | RTU1 | 2024-05-19 21:14:47 | Compressor run ignoring free cooling Opportunity of 10.97 kWh
WLLS1 | RTU1 | 2024-05-19 22:14:40 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-05-19 22:29:49 | Compressor run ignoring free cooling Opportunity of 8.65 kWh
WLLS1 | RTU1 | 2024-05-20 01:14:48 | Compressor run ignoring free cooling Opportunity of 5.18 kWh
WLLS1 | RTU1 | 2024-05-20 02:14:42 | Compressor run ignoring free cooling Opportunity of 10.02 kWh
WLLS1 | RTU1 | 2024-05-20 03:29:43 | Compressor run ignoring free cooling Opportunity of 4.68 kWh
WLLS1 | RTU1 | 2024-05-20 04:44:45 | Compressor run ignoring free cooling Opportunity of 10.26 kWh
WLLS1 | RTU1 | 2024-05-20 04:59:54 | Compressor run ignoring free cooling Opportunity of 5.29 kWh
WLLS1 | RTU1 | 2024-05-20 05:14:40 | Compressor run ignoring free cooling Opportunity of 4.48 kWh
WLLS1 | RTU1 | 2024-05-20 05:29:49 | Compressor run ignoring free cooling Opportunity of 10.42 kWh
WLLS1 | RTU1 | 2024-05-20 06:29:43 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-05-20 06:44:52 | Compressor run ignoring free cooling Opportunity of 8.48 kWh
WLLS1 | RTU1 | 2024-05-20 07:44:42 | Compressor run ignoring free cooling Opportunity of 10.55 kWh
WLLS1 | RTU1 | 2024-05-20 08:59:43 | Compressor run ignoring free cooling Opportunity of 9.88 kWh
WLLS1 | RTU1 | 2024-05-20 09:14:52 | Compressor run ignoring free cooling Opportunity of 10.80 kWh
WLLS1 | RTU1 | 2024-05-20 10:14:44 | Compressor run ignoring free cooling Opportunity of 10.68 kWh
WLLS1 | RTU1 | 2024-05-20 11:29:43 | Compressor run ignoring free cooling Opportunity of 9.79 kWh
WLLS1 | RTU1 | 2024-05-20 19:59:45 | Compressor run ignoring free cooling Opportunity of 10.73 kWh
WLLS1 | RTU1 | 2024-05-20 21:14:46 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-05-20 22:29:46 | Compressor run ignoring free cooling Opportunity of 9.73 kWh
WLLS1 | RTU1 | 2024-05-21 01:14:43 | Compressor run ignoring free cooling Opportunity of 5.09 kWh
WLLS1 | RTU1 | 2024-05-21 01:29:52 | Compressor run ignoring free cooling Opportunity of 4.80 kWh
WLLS1 | RTU1 | 2024-05-21 02:29:43 | Compressor run ignoring free cooling Opportunity of 9.84 kWh
WLLS1 | RTU1 | 2024-05-21 03:44:42 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-05-21 03:59:51 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU1 | 2024-05-21 05:44:44 | Compressor run ignoring free cooling Opportunity of 5.09 kWh
WLLS1 | RTU1 | 2024-05-21 06:59:42 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-05-21 07:14:51 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-05-21 08:14:43 | Compressor run ignoring free cooling Opportunity of 10.84 kWh
WLLS1 | RTU1 | 2024-05-21 22:14:41 | Compressor run ignoring free cooling Opportunity of 10.44 kWh
WLLS1 | RTU1 | 2024-05-21 22:29:45 | Compressor run ignoring free cooling Opportunity of 10.60 kWh
WLLS1 | RTU1 | 2024-05-21 22:44:48 | Compressor run ignoring free cooling Opportunity of 10.53 kWh
WLLS1 | RTU1 | 2024-05-21 22:59:53 | Compressor run ignoring free cooling Opportunity of 10.77 kWh
WLLS1 | RTU1 | 2024-05-21 23:14:55 | Compressor run ignoring free cooling Opportunity of 10.33 kWh
WLLS1 | RTU1 | 2024-05-21 23:29:58 | Compressor run ignoring free cooling Opportunity of 10.31 kWh
WLLS1 | RTU1 | 2024-05-21 23:44:40 | Compressor run ignoring free cooling Opportunity of 8.92 kWh
WLLS1 | RTU1 | 2024-05-22 02:14:40 | Compressor run ignoring free cooling Opportunity of 8.74 kWh
WLLS1 | RTU1 | 2024-05-22 02:29:44 | Compressor run ignoring free cooling Opportunity of 8.92 kWh
WLLS1 | RTU1 | 2024-05-22 02:44:47 | Compressor run ignoring free cooling Opportunity of 8.54 kWh
WLLS1 | RTU1 | 2024-05-22 02:59:52 | Compressor run ignoring free cooling Opportunity of 8.52 kWh
WLLS1 | RTU1 | 2024-05-22 03:14:55 | Compressor run ignoring free cooling Opportunity of 8.54 kWh
WLLS1 | RTU1 | 2024-05-22 05:14:57 | Compressor run ignoring free cooling Opportunity of 4.82 kWh
WLLS1 | RTU1 | 2024-05-22 07:29:45 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-05-22 07:44:47 | Compressor run ignoring free cooling Opportunity of 10.24 kWh
WLLS1 | RTU1 | 2024-05-22 07:59:52 | Compressor run ignoring free cooling Opportunity of 10.60 kWh
WLLS1 | RTU1 | 2024-05-22 08:14:55 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-05-22 08:29:57 | Compressor run ignoring free cooling Opportunity of 10.51 kWh
WLLS1 | RTU1 | 2024-05-22 22:59:41 | Compressor run ignoring free cooling Opportunity of 10.80 kWh
WLLS1 | RTU1 | 2024-05-22 23:14:45 | Compressor run ignoring free cooling Opportunity of 10.73 kWh
WLLS1 | RTU1 | 2024-05-23 00:14:51 | Compressor run ignoring free cooling Opportunity of 8.79 kWh
WLLS1 | RTU1 | 2024-05-23 00:29:58 | Compressor run ignoring free cooling Opportunity of 10.26 kWh
WLLS1 | RTU1 | 2024-05-23 02:59:41 | Compressor run ignoring free cooling Opportunity of 10.28 kWh
WLLS1 | RTU1 | 2024-05-23 03:14:46 | Compressor run ignoring free cooling Opportunity of 10.55 kWh
WLLS1 | RTU1 | 2024-05-23 03:29:51 | Compressor run ignoring free cooling Opportunity of 10.62 kWh
WLLS1 | RTU1 | 2024-05-23 03:44:54 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-05-23 03:59:58 | Compressor run ignoring free cooling Opportunity of 10.33 kWh
WLLS1 | RTU1 | 2024-05-23 05:14:49 | Compressor run ignoring free cooling Opportunity of 10.15 kWh
WLLS1 | RTU1 | 2024-05-23 05:29:52 | Compressor run ignoring free cooling Opportunity of 8.52 kWh
WLLS1 | RTU1 | 2024-05-23 05:44:55 | Compressor run ignoring free cooling Opportunity of 8.54 kWh
WLLS1 | RTU1 | 2024-05-23 07:59:39 | Compressor run ignoring free cooling Opportunity of 10.82 kWh
WLLS1 | RTU1 | 2024-05-23 19:29:54 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-05-23 19:44:58 | Compressor run ignoring free cooling Opportunity of 10.06 kWh
WLLS1 | RTU1 | 2024-05-23 21:29:44 | Compressor run ignoring free cooling Opportunity of 10.28 kWh
WLLS1 | RTU1 | 2024-05-23 21:44:47 | Compressor run ignoring free cooling Opportunity of 10.60 kWh
WLLS1 | RTU1 | 2024-05-23 21:59:50 | Compressor run ignoring free cooling Opportunity of 10.73 kWh
WLLS1 | RTU1 | 2024-05-23 22:14:54 | Compressor run ignoring free cooling Opportunity of 10.73 kWh
WLLS1 | RTU1 | 2024-05-23 22:29:57 | Compressor run ignoring free cooling Opportunity of 10.73 kWh
WLLS1 | RTU1 | 2024-05-23 23:44:51 | Compressor run ignoring free cooling Opportunity of 10.77 kWh
WLLS1 | RTU1 | 2024-05-24 01:14:43 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-05-24 01:29:48 | Compressor run ignoring free cooling Opportunity of 10.46 kWh
WLLS1 | RTU1 | 2024-05-24 01:44:53 | Compressor run ignoring free cooling Opportunity of 10.51 kWh
WLLS1 | RTU1 | 2024-05-24 04:29:43 | Compressor run ignoring free cooling Opportunity of 10.71 kWh
WLLS1 | RTU1 | 2024-05-24 04:44:48 | Compressor run ignoring free cooling Opportunity of 10.39 kWh
WLLS1 | RTU1 | 2024-05-24 05:44:43 | Compressor run ignoring free cooling Opportunity of 10.19 kWh
WLLS1 | RTU1 | 2024-05-24 05:59:45 | Compressor run ignoring free cooling Opportunity of 10.39 kWh
WLLS1 | RTU1 | 2024-05-24 06:14:50 | Compressor run ignoring free cooling Opportunity of 9.97 kWh
WLLS1 | RTU1 | 2024-05-24 06:29:53 | Compressor run ignoring free cooling Opportunity of 10.77 kWh
WLLS1 | RTU1 | 2024-05-24 06:44:56 | Compressor run ignoring free cooling Opportunity of 11.04 kWh
WLLS1 | RTU1 | 2024-05-24 08:59:40 | Compressor run ignoring free cooling Opportunity of 10.86 kWh
WLLS1 | RTU1 | 2024-05-24 19:44:46 | Compressor run ignoring free cooling Opportunity of 10.71 kWh
WLLS1 | RTU1 | 2024-05-24 19:59:50 | Compressor run ignoring free cooling Opportunity of 10.73 kWh
WLLS1 | RTU1 | 2024-05-24 20:14:53 | Compressor run ignoring free cooling Opportunity of 10.57 kWh
WLLS1 | RTU1 | 2024-05-24 20:29:57 | Compressor run ignoring free cooling Opportunity of 10.42 kWh
WLLS1 | RTU1 | 2024-05-24 22:14:42 | Compressor run ignoring free cooling Opportunity of 10.44 kWh
WLLS1 | RTU1 | 2024-05-24 22:29:46 | Compressor run ignoring free cooling Opportunity of 10.75 kWh
WLLS1 | RTU1 | 2024-05-24 22:44:48 | Compressor run ignoring free cooling Opportunity of 10.68 kWh
WLLS1 | RTU1 | 2024-05-24 22:59:53 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-05-24 23:44:41 | Compressor run ignoring free cooling Opportunity of 10.55 kWh
WLLS1 | RTU1 | 2024-05-25 02:14:44 | Compressor run ignoring free cooling Opportunity of 8.79 kWh
WLLS1 | RTU1 | 2024-05-25 02:29:48 | Compressor run ignoring free cooling Opportunity of 8.81 kWh
WLLS1 | RTU1 | 2024-05-25 02:44:52 | Compressor run ignoring free cooling Opportunity of 8.81 kWh
WLLS1 | RTU1 | 2024-05-25 02:59:56 | Compressor run ignoring free cooling Opportunity of 9.64 kWh
WLLS1 | RTU1 | 2024-05-25 06:44:40 | Compressor run ignoring free cooling Opportunity of 10.77 kWh
WLLS1 | RTU1 | 2024-05-25 06:59:44 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-05-25 07:14:46 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-05-25 07:29:50 | Compressor run ignoring free cooling Opportunity of 10.46 kWh
WLLS1 | RTU1 | 2024-05-25 19:44:42 | Compressor run ignoring free cooling Opportunity of 10.35 kWh
WLLS1 | RTU1 | 2024-05-25 19:59:48 | Compressor run ignoring free cooling Opportunity of 10.68 kWh
WLLS1 | RTU1 | 2024-05-25 20:14:51 | Compressor run ignoring free cooling Opportunity of 10.62 kWh
WLLS1 | RTU1 | 2024-05-25 20:29:55 | Compressor run ignoring free cooling Opportunity of 9.61 kWh
WLLS1 | RTU1 | 2024-05-25 20:44:58 | Compressor run ignoring free cooling Opportunity of 8.54 kWh
WLLS1 | RTU1 | 2024-05-25 23:14:44 | Compressor run ignoring free cooling Opportunity of 10.97 kWh
WLLS1 | RTU1 | 2024-05-26 02:29:44 | Compressor run ignoring free cooling Opportunity of 10.60 kWh
WLLS1 | RTU1 | 2024-05-26 02:44:48 | Compressor run ignoring free cooling Opportunity of 10.48 kWh
WLLS1 | RTU1 | 2024-05-26 02:59:54 | Compressor run ignoring free cooling Opportunity of 10.84 kWh
WLLS1 | RTU1 | 2024-05-26 03:14:57 | Compressor run ignoring free cooling Opportunity of 10.84 kWh
WLLS1 | RTU1 | 2024-05-27 00:14:51 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-05-27 00:29:54 | Compressor run ignoring free cooling Opportunity of 10.22 kWh
WLLS1 | RTU1 | 2024-05-27 00:44:57 | Compressor run ignoring free cooling Opportunity of 10.75 kWh
WLLS1 | RTU1 | 2024-05-27 03:29:44 | Compressor run ignoring free cooling Opportunity of 10.71 kWh
WLLS1 | RTU1 | 2024-05-27 03:44:47 | Compressor run ignoring free cooling Opportunity of 10.10 kWh
WLLS1 | RTU1 | 2024-05-27 03:59:50 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-05-27 04:14:55 | Compressor run ignoring free cooling Opportunity of 10.68 kWh
WLLS1 | RTU1 | 2024-05-27 05:14:49 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-05-27 05:29:54 | Compressor run ignoring free cooling Opportunity of 10.66 kWh
WLLS1 | RTU1 | 2024-05-27 05:44:56 | Compressor run ignoring free cooling Opportunity of 10.28 kWh
WLLS1 | RTU1 | 2024-05-27 07:59:41 | Compressor run ignoring free cooling Opportunity of 10.55 kWh
WLLS1 | RTU1 | 2024-05-27 08:14:43 | Compressor run ignoring free cooling Opportunity of 10.71 kWh
WLLS1 | RTU1 | 2024-05-27 08:29:47 | Compressor run ignoring free cooling Opportunity of 10.64 kWh
WLLS1 | RTU1 | 2024-05-27 08:44:51 | Compressor run ignoring free cooling Opportunity of 10.86 kWh
WLLS1 | RTU1 | 2024-05-27 08:59:54 | Compressor run ignoring free cooling Opportunity of 10.60 kWh
WLLS1 | RTU1 | 2024-05-27 09:14:56 | Compressor run ignoring free cooling Opportunity of 8.77 kWh
WLLS1 | RTU1 | 2024-05-28 22:29:41 | Compressor run ignoring free cooling Opportunity of 10.10 kWh
WLLS1 | RTU1 | 2024-05-29 20:44:54 | Compressor run ignoring free cooling Opportunity of 4.37 kWh
WLLS1 | RTU1 | 2024-05-30 00:14:48 | Compressor run ignoring free cooling Opportunity of 8.19 kWh
WLLS1 | RTU1 | 2024-05-30 00:29:52 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-05-30 00:44:55 | Compressor run ignoring free cooling Opportunity of 8.16 kWh
WLLS1 | RTU1 | 2024-05-30 00:59:59 | Compressor run ignoring free cooling Opportunity of 4.91 kWh
WLLS1 | RTU1 | 2024-05-30 03:29:43 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-05-30 03:44:48 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-05-30 03:59:51 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-05-30 04:14:56 | Compressor run ignoring free cooling Opportunity of 5.02 kWh
WLLS1 | RTU1 | 2024-05-30 05:14:49 | Compressor run ignoring free cooling Opportunity of 4.84 kWh
WLLS1 | RTU1 | 2024-05-30 05:29:53 | Compressor run ignoring free cooling Opportunity of 4.84 kWh
WLLS1 | RTU1 | 2024-05-30 08:44:41 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-05-30 08:59:45 | Compressor run ignoring free cooling Opportunity of 8.54 kWh
WLLS1 | RTU1 | 2024-05-30 09:14:50 | Compressor run ignoring free cooling Opportunity of 8.48 kWh
WLLS1 | RTU1 | 2024-05-30 21:59:40 | Compressor run ignoring free cooling Opportunity of 4.84 kWh
WLLS1 | RTU1 | 2024-05-30 22:14:43 | Compressor run ignoring free cooling Opportunity of 4.68 kWh
WLLS1 | RTU1 | 2024-05-30 22:29:47 | Compressor run ignoring free cooling Opportunity of 4.71 kWh
WLLS1 | RTU1 | 2024-05-30 22:44:50 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-05-30 22:59:52 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-05-30 23:14:55 | Compressor run ignoring free cooling Opportunity of 4.95 kWh
WLLS1 | RTU1 | 2024-05-31 01:44:40 | Compressor run ignoring free cooling Opportunity of 5.11 kWh
WLLS1 | RTU1 | 2024-05-31 01:59:42 | Compressor run ignoring free cooling Opportunity of 5.09 kWh
WLLS1 | RTU1 | 2024-05-31 02:14:45 | Compressor run ignoring free cooling Opportunity of 5.02 kWh
WLLS1 | RTU1 | 2024-05-31 02:29:48 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-05-31 02:44:50 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-05-31 02:59:54 | Compressor run ignoring free cooling Opportunity of 4.73 kWh
WLLS1 | RTU1 | 2024-05-31 07:14:43 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-05-31 07:29:48 | Compressor run ignoring free cooling Opportunity of 5.24 kWh
WLLS1 | RTU1 | 2024-05-31 07:44:52 | Compressor run ignoring free cooling Opportunity of 5.00 kWh
WLLS1 | RTU1 | 2024-05-31 07:59:55 | Compressor run ignoring free cooling Opportunity of 4.75 kWh
WLLS1 | RTU1 | 2024-05-31 08:14:57 | Compressor run ignoring free cooling Opportunity of 4.86 kWh
WLLS1 | RTU1 | 2024-05-31 09:44:41 | Compressor run ignoring free cooling Opportunity of 4.68 kWh
WLLS1 | RTU1 | 2024-05-31 09:59:48 | Compressor run ignoring free cooling Opportunity of 3.28 kWh
WLLS1 | RTU1 | 2024-05-31 19:44:44 | Compressor run ignoring free cooling Opportunity of 4.93 kWh
WLLS1 | RTU1 | 2024-05-31 19:59:48 | Compressor run ignoring free cooling Opportunity of 4.84 kWh
WLLS1 | RTU1 | 2024-05-31 20:14:51 | Compressor run ignoring free cooling Opportunity of 4.82 kWh
WLLS1 | RTU1 | 2024-05-31 20:29:53 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-05-31 20:44:56 | Compressor run ignoring free cooling Opportunity of 4.62 kWh
WLLS1 | RTU1 | 2024-05-31 23:14:42 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU1 | 2024-01-25 13:15:01 | Compressor run ignoring free heating Opportunity of 10.06 kWh
WLLS1 | RTU10 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU10 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU10 | 2024-05-24 19:59:54 | Compressor run ignoring free cooling Opportunity of 5.51 kWh
WLLS1 | RTU10 | 2024-05-24 20:14:57 | Compressor run ignoring free cooling Opportunity of 5.49 kWh
WLLS1 | RTU10 | 2024-05-31 23:14:46 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU11 | 2024-01-06 15:14:52 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-05 05:44:56 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-05 15:44:51 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-05 17:59:55 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-05 20:14:58 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-06 11:30:00 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-06 11:59:52 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-06 14:00:00 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-06 16:29:57 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-06 19:14:56 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-07 01:29:56 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-07 07:44:58 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-07 08:14:49 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-07 12:44:58 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-07 18:14:53 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-07 20:29:58 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-08 19:00:01 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-12 15:14:54 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-13 15:15:02 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-13 15:44:54 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-13 17:59:59 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-13 18:29:52 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-14 14:14:57 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-14 22:14:59 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-15 08:45:00 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-15 13:44:55 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-15 16:14:54 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-16 17:59:53 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-16 20:14:57 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-16 22:59:55 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-17 16:59:56 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-17 21:44:56 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-18 00:45:03 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-18 01:14:53 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-04-20 15:44:55 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-04-21 08:44:54 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-04-21 21:14:55 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-04-23 19:29:54 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-04-27 16:29:55 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-04-29 14:59:54 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-07 23:45:04 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-09 13:59:53 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-09 15:44:58 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-09 17:29:57 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-17 00:44:53 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-19 17:44:54 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-21 13:44:57 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-22 11:30:01 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-23 12:44:59 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-24 04:44:52 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-24 19:29:47 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-24 20:14:57 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-24 22:59:57 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-25 03:00:00 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-25 10:29:50 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-25 10:59:59 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-26 03:15:01 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-29 12:29:46 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-29 12:59:52 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-29 13:29:59 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-29 16:29:51 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-29 16:59:57 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-29 20:14:53 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-29 20:44:58 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-30 00:29:56 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-30 03:44:52 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-30 18:29:48 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-30 18:59:57 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-30 19:30:03 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-30 22:59:57 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-31 12:59:54 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-31 16:14:51 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-31 16:44:58 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-31 19:59:52 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-05-31 20:29:58 | Unit Quick ON/Off within 15 min
WLLS1 | RTU11 | 2024-03-06 11:44:55 | Short Cycling Detected
WLLS1 | RTU11 | 2024-03-06 19:29:50 | Short Cycling Detected
WLLS1 | RTU11 | 2024-03-07 07:59:53 | Short Cycling Detected
WLLS1 | RTU11 | 2024-03-07 20:44:52 | Short Cycling Detected
WLLS1 | RTU11 | 2024-03-08 19:14:56 | Short Cycling Detected
WLLS1 | RTU11 | 2024-03-12 15:29:49 | Short Cycling Detected
WLLS1 | RTU11 | 2024-03-13 15:59:51 | Short Cycling Detected
WLLS1 | RTU11 | 2024-03-13 18:14:57 | Short Cycling Detected
WLLS1 | RTU11 | 2024-03-14 14:29:53 | Short Cycling Detected
WLLS1 | RTU11 | 2024-03-16 20:29:52 | Short Cycling Detected
WLLS1 | RTU11 | 2024-03-17 17:14:51 | Short Cycling Detected
WLLS1 | RTU11 | 2024-03-18 00:59:57 | Short Cycling Detected
WLLS1 | RTU11 | 2024-05-25 10:44:53 | Short Cycling Detected
WLLS1 | RTU11 | 2024-05-29 13:14:56 | Short Cycling Detected
WLLS1 | RTU11 | 2024-05-29 16:44:54 | Short Cycling Detected
WLLS1 | RTU11 | 2024-05-29 17:15:00 | Short Cycling Detected
WLLS1 | RTU11 | 2024-05-30 00:44:59 | Short Cycling Detected
WLLS1 | RTU11 | 2024-05-30 03:59:56 | Short Cycling Detected
WLLS1 | RTU11 | 2024-05-30 19:15:00 | Short Cycling Detected
WLLS1 | RTU11 | 2024-05-31 16:29:55 | Short Cycling Detected
WLLS1 | RTU11 | 2024-05-31 17:00:01 | Short Cycling Detected
WLLS1 | RTU11 | 2024-05-31 20:14:55 | Short Cycling Detected
WLLS1 | RTU11 | 2024-05-31 20:45:00 | Short Cycling Detected
WLLS1 | RTU11 | 2024-04-11 12:59:48 | Compressor run ignoring free cooling Opportunity of 3.39 kWh
WLLS1 | RTU11 | 2024-04-11 19:59:44 | Compressor run ignoring free cooling Opportunity of 3.31 kWh
WLLS1 | RTU11 | 2024-04-11 22:59:49 | Compressor run ignoring free cooling Opportunity of 3.44 kWh
WLLS1 | RTU11 | 2024-04-30 02:29:44 | Compressor run ignoring free cooling Opportunity of 3.36 kWh
WLLS1 | RTU11 | 2024-04-30 05:29:48 | Compressor run ignoring free cooling Opportunity of 3.38 kWh
WLLS1 | RTU11 | 2024-04-30 22:44:50 | Compressor run ignoring free cooling Opportunity of 3.47 kWh
WLLS1 | RTU11 | 2024-05-01 01:29:56 | Compressor run ignoring free cooling Opportunity of 3.33 kWh
WLLS1 | RTU11 | 2024-05-01 21:15:04 | Compressor run ignoring free cooling Opportunity of 3.31 kWh
WLLS1 | RTU11 | 2024-05-05 03:15:03 | Compressor run ignoring free cooling Opportunity of 3.27 kWh
WLLS1 | RTU11 | 2024-05-05 22:45:03 | Compressor run ignoring free cooling Opportunity of 3.37 kWh
WLLS1 | RTU11 | 2024-05-09 00:29:51 | Compressor run ignoring free cooling Opportunity of 3.54 kWh
WLLS1 | RTU11 | 2024-05-09 02:59:45 | Compressor run ignoring free cooling Opportunity of 3.46 kWh
WLLS1 | RTU11 | 2024-05-09 04:44:56 | Compressor run ignoring free cooling Opportunity of 3.48 kWh
WLLS1 | RTU11 | 2024-05-10 23:59:57 | Compressor run ignoring free cooling Opportunity of 3.03 kWh
WLLS1 | RTU11 | 2024-05-11 23:00:02 | Compressor run ignoring free cooling Opportunity of 3.19 kWh
WLLS1 | RTU11 | 2024-05-15 19:44:46 | Compressor run ignoring free cooling Opportunity of 3.33 kWh
WLLS1 | RTU11 | 2024-05-16 20:44:45 | Compressor run ignoring free cooling Opportunity of 3.47 kWh
WLLS1 | RTU11 | 2024-05-17 01:59:51 | Compressor run ignoring free cooling Opportunity of 3.48 kWh
WLLS1 | RTU11 | 2024-05-19 02:44:53 | Compressor run ignoring free cooling Opportunity of 2.98 kWh
WLLS1 | RTU11 | 2024-05-19 11:44:48 | Compressor run ignoring free cooling Opportunity of 3.31 kWh
WLLS1 | RTU11 | 2024-05-21 01:14:47 | Compressor run ignoring free cooling Opportunity of 3.23 kWh
WLLS1 | RTU11 | 2024-05-23 05:29:56 | Compressor run ignoring free cooling Opportunity of 3.39 kWh
WLLS1 | RTU11 | 2024-05-23 07:59:44 | Compressor run ignoring free cooling Opportunity of 3.41 kWh
WLLS1 | RTU11 | 2024-05-23 21:29:48 | Compressor run ignoring free cooling Opportunity of 3.35 kWh
WLLS1 | RTU11 | 2024-05-23 22:30:01 | Compressor run ignoring free cooling Opportunity of 3.40 kWh
WLLS1 | RTU11 | 2024-05-24 01:14:47 | Compressor run ignoring free cooling Opportunity of 3.31 kWh
WLLS1 | RTU11 | 2024-05-24 22:29:50 | Compressor run ignoring free cooling Opportunity of 2.48 kWh
WLLS1 | RTU11 | 2024-05-25 19:59:52 | Compressor run ignoring free cooling Opportunity of 3.37 kWh
WLLS1 | RTU11 | 2024-05-31 23:14:46 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU12 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU12 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU12 | 2024-03-18 15:29:57 | No findings on Compressor being run ignoring free cooling Opportunity
WLLS1 | RTU12 | 2024-01-09 17:59:55 | Compressor run ignoring free heating Opportunity of 2.41 kWh
WLLS1 | RTU12 | 2024-01-13 00:14:59 | Compressor run ignoring free heating Opportunity of 4.15 kWh
WLLS1 | RTU12 | 2024-01-13 00:30:02 | Compressor run ignoring free heating Opportunity of 4.23 kWh
WLLS1 | RTU12 | 2024-01-13 00:45:03 | Compressor run ignoring free heating Opportunity of 4.19 kWh
WLLS1 | RTU12 | 2024-01-13 01:00:03 | Compressor run ignoring free heating Opportunity of 4.39 kWh
WLLS1 | RTU12 | 2024-01-13 02:30:06 | Compressor run ignoring free heating Opportunity of 4.49 kWh
WLLS1 | RTU12 | 2024-03-04 12:45:05 | Compressor run ignoring free heating Opportunity of 4.95 kWh
WLLS1 | RTU12 | 2024-03-04 13:00:00 | Compressor run ignoring free heating Opportunity of 4.93 kWh
WLLS1 | RTU12 | 2024-03-04 13:14:56 | Compressor run ignoring free heating Opportunity of 4.91 kWh
WLLS1 | RTU12 | 2024-03-04 13:29:51 | Compressor run ignoring free heating Opportunity of 4.91 kWh
WLLS1 | RTU12 | 2024-03-04 15:15:05 | Compressor run ignoring free heating Opportunity of 4.91 kWh
WLLS1 | RTU12 | 2024-03-04 15:29:59 | Compressor run ignoring free heating Opportunity of 4.92 kWh
WLLS1 | RTU12 | 2024-03-04 15:44:56 | Compressor run ignoring free heating Opportunity of 4.91 kWh
WLLS1 | RTU12 | 2024-03-04 15:59:51 | Compressor run ignoring free heating Opportunity of 4.91 kWh
WLLS1 | RTU12 | 2024-03-05 12:59:52 | Compressor run ignoring free heating Opportunity of 4.93 kWh
WLLS1 | RTU12 | 2024-03-05 14:45:06 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-05 15:00:03 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-05 15:15:00 | Compressor run ignoring free heating Opportunity of 4.95 kWh
WLLS1 | RTU12 | 2024-03-05 15:29:56 | Compressor run ignoring free heating Opportunity of 4.94 kWh
WLLS1 | RTU12 | 2024-03-05 15:44:51 | Compressor run ignoring free heating Opportunity of 4.93 kWh
WLLS1 | RTU12 | 2024-03-07 10:00:04 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-07 10:14:59 | Compressor run ignoring free heating Opportunity of 5.00 kWh
WLLS1 | RTU12 | 2024-03-07 10:29:53 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-07 12:30:03 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-07 12:44:58 | Compressor run ignoring free heating Opportunity of 4.92 kWh
WLLS1 | RTU12 | 2024-03-07 12:59:54 | Compressor run ignoring free heating Opportunity of 4.91 kWh
WLLS1 | RTU12 | 2024-03-07 13:14:51 | Compressor run ignoring free heating Opportunity of 4.94 kWh
WLLS1 | RTU12 | 2024-03-07 15:00:04 | Compressor run ignoring free heating Opportunity of 5.00 kWh
WLLS1 | RTU12 | 2024-03-07 15:14:59 | Compressor run ignoring free heating Opportunity of 4.99 kWh
WLLS1 | RTU12 | 2024-03-07 15:29:57 | Compressor run ignoring free heating Opportunity of 4.96 kWh
WLLS1 | RTU12 | 2024-03-07 15:44:51 | Compressor run ignoring free heating Opportunity of 4.95 kWh
WLLS1 | RTU12 | 2024-03-07 17:30:05 | Compressor run ignoring free heating Opportunity of 4.92 kWh
WLLS1 | RTU12 | 2024-03-07 17:45:00 | Compressor run ignoring free heating Opportunity of 4.90 kWh
WLLS1 | RTU12 | 2024-03-08 13:45:03 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-08 13:59:59 | Compressor run ignoring free heating Opportunity of 4.96 kWh
WLLS1 | RTU12 | 2024-03-08 14:14:58 | Compressor run ignoring free heating Opportunity of 4.94 kWh
WLLS1 | RTU12 | 2024-03-08 14:29:55 | Compressor run ignoring free heating Opportunity of 4.93 kWh
WLLS1 | RTU12 | 2024-03-12 12:30:05 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-12 12:45:02 | Compressor run ignoring free heating Opportunity of 4.99 kWh
WLLS1 | RTU12 | 2024-03-12 13:00:00 | Compressor run ignoring free heating Opportunity of 5.00 kWh
WLLS1 | RTU12 | 2024-03-12 14:45:04 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-12 14:59:59 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-12 15:14:54 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-12 15:29:49 | Compressor run ignoring free heating Opportunity of 4.94 kWh
WLLS1 | RTU12 | 2024-03-12 17:15:04 | Compressor run ignoring free heating Opportunity of 4.93 kWh
WLLS1 | RTU12 | 2024-03-12 17:29:58 | Compressor run ignoring free heating Opportunity of 4.92 kWh
WLLS1 | RTU12 | 2024-03-12 17:44:53 | Compressor run ignoring free heating Opportunity of 4.91 kWh
WLLS1 | RTU12 | 2024-03-13 10:14:58 | Compressor run ignoring free heating Opportunity of 4.99 kWh
WLLS1 | RTU12 | 2024-03-13 10:29:53 | Compressor run ignoring free heating Opportunity of 5.00 kWh
WLLS1 | RTU12 | 2024-03-13 12:15:05 | Compressor run ignoring free heating Opportunity of 5.00 kWh
WLLS1 | RTU12 | 2024-03-13 12:30:01 | Compressor run ignoring free heating Opportunity of 4.99 kWh
WLLS1 | RTU12 | 2024-03-13 12:44:58 | Compressor run ignoring free heating Opportunity of 5.00 kWh
WLLS1 | RTU12 | 2024-03-13 12:59:54 | Compressor run ignoring free heating Opportunity of 5.00 kWh
WLLS1 | RTU12 | 2024-03-13 15:00:05 | Compressor run ignoring free heating Opportunity of 4.95 kWh
WLLS1 | RTU12 | 2024-03-13 15:15:02 | Compressor run ignoring free heating Opportunity of 4.95 kWh
WLLS1 | RTU12 | 2024-03-13 15:30:00 | Compressor run ignoring free heating Opportunity of 4.95 kWh
WLLS1 | RTU12 | 2024-03-13 15:44:54 | Compressor run ignoring free heating Opportunity of 4.94 kWh
WLLS1 | RTU12 | 2024-03-13 15:59:51 | Compressor run ignoring free heating Opportunity of 4.94 kWh
WLLS1 | RTU12 | 2024-03-13 17:45:04 | Compressor run ignoring free heating Opportunity of 4.93 kWh
WLLS1 | RTU12 | 2024-03-13 17:59:59 | Compressor run ignoring free heating Opportunity of 4.93 kWh
WLLS1 | RTU12 | 2024-03-13 18:14:57 | Compressor run ignoring free heating Opportunity of 4.91 kWh
WLLS1 | RTU12 | 2024-03-13 18:29:51 | Compressor run ignoring free heating Opportunity of 4.90 kWh
WLLS1 | RTU12 | 2024-03-14 11:30:01 | Compressor run ignoring free heating Opportunity of 4.99 kWh
WLLS1 | RTU12 | 2024-03-14 11:44:57 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-14 11:59:52 | Compressor run ignoring free heating Opportunity of 4.99 kWh
WLLS1 | RTU12 | 2024-03-14 13:45:04 | Compressor run ignoring free heating Opportunity of 4.95 kWh
WLLS1 | RTU12 | 2024-03-14 14:00:01 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-14 14:14:57 | Compressor run ignoring free heating Opportunity of 4.96 kWh
WLLS1 | RTU12 | 2024-03-14 14:29:53 | Compressor run ignoring free heating Opportunity of 4.96 kWh
WLLS1 | RTU12 | 2024-03-14 16:30:05 | Compressor run ignoring free heating Opportunity of 4.94 kWh
WLLS1 | RTU12 | 2024-03-14 16:45:01 | Compressor run ignoring free heating Opportunity of 4.94 kWh
WLLS1 | RTU12 | 2024-03-14 16:59:55 | Compressor run ignoring free heating Opportunity of 4.93 kWh
WLLS1 | RTU12 | 2024-03-14 17:14:51 | Compressor run ignoring free heating Opportunity of 4.93 kWh
WLLS1 | RTU12 | 2024-03-14 19:00:05 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-14 19:15:02 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-14 19:29:58 | Compressor run ignoring free heating Opportunity of 4.87 kWh
WLLS1 | RTU12 | 2024-03-14 19:44:53 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-14 19:59:48 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-14 22:00:02 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-14 22:14:59 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-14 22:29:57 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-14 22:44:52 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-14 23:45:05 | Compressor run ignoring free heating Opportunity of 4.87 kWh
WLLS1 | RTU12 | 2024-03-15 02:00:02 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-15 02:14:58 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-15 02:29:53 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-15 04:30:02 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-15 04:44:57 | Compressor run ignoring free heating Opportunity of 4.87 kWh
WLLS1 | RTU12 | 2024-03-15 10:45:05 | Compressor run ignoring free heating Opportunity of 4.95 kWh
WLLS1 | RTU12 | 2024-03-15 11:00:01 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-15 11:14:57 | Compressor run ignoring free heating Opportunity of 4.95 kWh
WLLS1 | RTU12 | 2024-03-15 11:29:51 | Compressor run ignoring free heating Opportunity of 4.95 kWh
WLLS1 | RTU12 | 2024-03-15 13:15:05 | Compressor run ignoring free heating Opportunity of 4.92 kWh
WLLS1 | RTU12 | 2024-03-15 13:30:01 | Compressor run ignoring free heating Opportunity of 4.92 kWh
WLLS1 | RTU12 | 2024-03-15 13:44:55 | Compressor run ignoring free heating Opportunity of 4.93 kWh
WLLS1 | RTU12 | 2024-03-15 13:59:49 | Compressor run ignoring free heating Opportunity of 4.92 kWh
WLLS1 | RTU12 | 2024-03-15 15:45:03 | Compressor run ignoring free heating Opportunity of 4.92 kWh
WLLS1 | RTU12 | 2024-03-15 15:59:58 | Compressor run ignoring free heating Opportunity of 4.91 kWh
WLLS1 | RTU12 | 2024-03-15 16:14:54 | Compressor run ignoring free heating Opportunity of 4.91 kWh
WLLS1 | RTU12 | 2024-03-15 18:15:00 | Compressor run ignoring free heating Opportunity of 4.91 kWh
WLLS1 | RTU12 | 2024-03-15 18:29:55 | Compressor run ignoring free heating Opportunity of 4.90 kWh
WLLS1 | RTU12 | 2024-03-15 18:44:53 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-15 20:45:04 | Compressor run ignoring free heating Opportunity of 4.86 kWh
WLLS1 | RTU12 | 2024-03-15 20:59:59 | Compressor run ignoring free heating Opportunity of 4.85 kWh
WLLS1 | RTU12 | 2024-03-16 02:30:03 | Compressor run ignoring free heating Opportunity of 4.82 kWh
WLLS1 | RTU12 | 2024-03-16 12:00:06 | Compressor run ignoring free heating Opportunity of 5.00 kWh
WLLS1 | RTU12 | 2024-03-16 12:15:00 | Compressor run ignoring free heating Opportunity of 4.99 kWh
WLLS1 | RTU12 | 2024-03-16 12:29:59 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-16 12:44:54 | Compressor run ignoring free heating Opportunity of 4.94 kWh
WLLS1 | RTU12 | 2024-03-16 12:59:49 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-16 14:45:05 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-16 15:00:02 | Compressor run ignoring free heating Opportunity of 4.95 kWh
WLLS1 | RTU12 | 2024-03-16 15:14:57 | Compressor run ignoring free heating Opportunity of 4.96 kWh
WLLS1 | RTU12 | 2024-03-16 15:29:53 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-16 17:30:02 | Compressor run ignoring free heating Opportunity of 4.90 kWh
WLLS1 | RTU12 | 2024-03-16 17:44:58 | Compressor run ignoring free heating Opportunity of 4.90 kWh
WLLS1 | RTU12 | 2024-03-16 17:59:53 | Compressor run ignoring free heating Opportunity of 4.91 kWh
WLLS1 | RTU12 | 2024-03-17 09:14:59 | Compressor run ignoring free heating Opportunity of 4.91 kWh
WLLS1 | RTU12 | 2024-03-17 09:29:56 | Compressor run ignoring free heating Opportunity of 4.92 kWh
WLLS1 | RTU12 | 2024-03-17 09:44:53 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-17 11:45:02 | Compressor run ignoring free heating Opportunity of 4.96 kWh
WLLS1 | RTU12 | 2024-03-17 11:59:57 | Compressor run ignoring free heating Opportunity of 4.94 kWh
WLLS1 | RTU12 | 2024-03-17 12:14:53 | Compressor run ignoring free heating Opportunity of 4.93 kWh
WLLS1 | RTU12 | 2024-03-17 14:15:02 | Compressor run ignoring free heating Opportunity of 4.97 kWh
WLLS1 | RTU12 | 2024-03-17 14:29:59 | Compressor run ignoring free heating Opportunity of 4.92 kWh
WLLS1 | RTU12 | 2024-03-17 14:44:54 | Compressor run ignoring free heating Opportunity of 4.92 kWh
WLLS1 | RTU12 | 2024-03-17 16:30:04 | Compressor run ignoring free heating Opportunity of 4.95 kWh
WLLS1 | RTU12 | 2024-03-17 16:45:02 | Compressor run ignoring free heating Opportunity of 4.92 kWh
WLLS1 | RTU12 | 2024-03-17 16:59:56 | Compressor run ignoring free heating Opportunity of 4.93 kWh
WLLS1 | RTU12 | 2024-03-17 17:14:51 | Compressor run ignoring free heating Opportunity of 4.92 kWh
WLLS1 | RTU12 | 2024-03-17 19:00:04 | Compressor run ignoring free heating Opportunity of 4.90 kWh
WLLS1 | RTU12 | 2024-03-17 19:15:00 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-17 19:29:56 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-17 21:15:04 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-17 21:30:00 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-17 21:44:56 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-18 00:30:06 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-18 00:45:03 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-18 00:59:57 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-18 01:14:53 | Compressor run ignoring free heating Opportunity of 4.89 kWh
WLLS1 | RTU12 | 2024-03-18 03:44:55 | Compressor run ignoring free heating Opportunity of 4.87 kWh
WLLS1 | RTU12 | 2024-03-18 03:59:52 | Compressor run ignoring free heating Opportunity of 4.87 kWh
WLLS1 | RTU13 | 2024-01-01 09:29:59 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-02 07:59:53 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-02 19:59:56 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-04 19:14:51 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-05 19:30:01 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-05 21:59:59 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-06 08:14:51 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-08 07:44:54 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-09 06:30:00 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-10 19:59:58 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-11 06:14:57 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-15 07:29:55 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-15 10:45:01 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-16 08:59:50 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-16 09:29:52 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-16 09:59:53 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-16 19:29:57 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-16 19:59:58 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-16 21:15:00 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-16 22:45:04 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-16 23:15:04 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-17 14:14:55 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-19 21:15:00 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-19 21:45:01 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-19 22:15:04 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-20 17:14:47 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-20 18:29:50 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-20 18:59:50 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-20 19:29:53 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-20 19:59:58 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-20 21:15:01 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-20 21:45:01 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-20 22:30:04 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-21 17:29:58 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-21 18:00:04 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-21 18:30:06 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-03-08 11:29:57 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-03-12 08:14:50 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-03-13 05:29:57 | Unit Quick ON/Off within 15 min
WLLS1 | RTU13 | 2024-01-05 19:44:56 | Short Cycling Detected
WLLS1 | RTU13 | 2024-01-05 22:14:53 | Short Cycling Detected
WLLS1 | RTU13 | 2024-01-11 06:29:53 | Short Cycling Detected
WLLS1 | RTU13 | 2024-01-16 09:14:50 | Short Cycling Detected
WLLS1 | RTU13 | 2024-01-16 09:44:53 | Short Cycling Detected
WLLS1 | RTU13 | 2024-01-16 10:14:53 | Short Cycling Detected
WLLS1 | RTU13 | 2024-01-16 21:30:01 | Short Cycling Detected
WLLS1 | RTU13 | 2024-01-19 22:30:04 | Short Cycling Detected
WLLS1 | RTU13 | 2024-01-20 17:29:49 | Short Cycling Detected
WLLS1 | RTU13 | 2024-01-20 18:44:50 | Short Cycling Detected
WLLS1 | RTU13 | 2024-01-20 19:14:52 | Short Cycling Detected
WLLS1 | RTU13 | 2024-01-20 19:44:55 | Short Cycling Detected
WLLS1 | RTU13 | 2024-01-20 21:30:01 | Short Cycling Detected
WLLS1 | RTU13 | 2024-01-20 22:45:04 | Short Cycling Detected
WLLS1 | RTU13 | 2024-01-21 18:15:05 | Short Cycling Detected
WLLS1 | RTU13 | 2024-03-13 05:44:54 | Short Cycling Detected
WLLS1 | RTU13 | 2024-01-03 05:30:03 | Compressor run ignoring free cooling Opportunity of 2.71 kWh
WLLS1 | RTU13 | 2024-01-03 05:44:57 | Compressor run ignoring free cooling Opportunity of 2.80 kWh
WLLS1 | RTU13 | 2024-01-03 08:00:03 | Compressor run ignoring free cooling Opportunity of 2.76 kWh
WLLS1 | RTU13 | 2024-01-05 05:14:54 | Compressor run ignoring free cooling Opportunity of 2.66 kWh
WLLS1 | RTU13 | 2024-01-05 07:15:04 | Compressor run ignoring free cooling Opportunity of 2.75 kWh
WLLS1 | RTU13 | 2024-01-05 07:29:59 | Compressor run ignoring free cooling Opportunity of 2.69 kWh
WLLS1 | RTU13 | 2024-01-05 07:44:56 | Compressor run ignoring free cooling Opportunity of 2.69 kWh
WLLS1 | RTU13 | 2024-01-06 05:14:57 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU13 | 2024-03-16 17:30:02 | Compressor run ignoring free heating Opportunity of 2.72 kWh
WLLS1 | RTU13 | 2024-03-16 17:44:57 | Compressor run ignoring free heating Opportunity of 2.74 kWh
WLLS1 | RTU15 | 2024-05-30 09:14:53 | Unit Quick ON/Off within 15 min
WLLS1 | RTU15 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU15 | 2024-01-05 07:15:04 | Compressor run ignoring free cooling Opportunity of 2.31 kWh
WLLS1 | RTU15 | 2024-01-05 07:29:59 | Compressor run ignoring free cooling Opportunity of 2.26 kWh
WLLS1 | RTU15 | 2024-01-21 07:30:01 | Compressor run ignoring free cooling Opportunity of 2.40 kWh
WLLS1 | RTU15 | 2024-01-21 07:45:01 | Compressor run ignoring free cooling Opportunity of 2.51 kWh
WLLS1 | RTU15 | 2024-03-07 10:14:59 | Compressor run ignoring free cooling Opportunity of 8.93 kWh
WLLS1 | RTU15 | 2024-03-07 12:30:02 | Compressor run ignoring free cooling Opportunity of 9.15 kWh
WLLS1 | RTU15 | 2024-03-07 12:44:57 | Compressor run ignoring free cooling Opportunity of 8.91 kWh
WLLS1 | RTU15 | 2024-03-08 13:45:03 | Compressor run ignoring free cooling Opportunity of 8.91 kWh
WLLS1 | RTU15 | 2024-04-02 08:29:50 | Compressor run ignoring free cooling Opportunity of 8.91 kWh
WLLS1 | RTU15 | 2024-04-02 08:44:54 | Compressor run ignoring free cooling Opportunity of 8.93 kWh
WLLS1 | RTU15 | 2024-04-09 11:29:46 | Compressor run ignoring free cooling Opportunity of 8.75 kWh
WLLS1 | RTU15 | 2024-04-10 08:44:45 | Compressor run ignoring free cooling Opportunity of 12.67 kWh
WLLS1 | RTU15 | 2024-04-23 12:59:47 | Compressor run ignoring free cooling Opportunity of 8.95 kWh
WLLS1 | RTU15 | 2024-04-25 11:14:44 | Compressor run ignoring free cooling Opportunity of 9.02 kWh
WLLS1 | RTU15 | 2024-04-25 11:29:54 | Compressor run ignoring free cooling Opportunity of 9.06 kWh
WLLS1 | RTU15 | 2024-05-14 09:59:50 | Compressor run ignoring free cooling Opportunity of 9.04 kWh
WLLS1 | RTU15 | 2024-05-20 10:14:47 | Compressor run ignoring free cooling Opportunity of 8.82 kWh
WLLS1 | RTU15 | 2024-05-30 08:44:45 | Compressor run ignoring free cooling Opportunity of 8.86 kWh
WLLS1 | RTU15 | 2024-05-31 20:14:55 | Compressor run ignoring free cooling Opportunity of 2.22 kWh
WLLS1 | RTU15 | 2024-05-31 23:14:46 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU16 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU16 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU16 | 2024-03-04 12:45:05 | Compressor run ignoring free cooling Opportunity of 8.53 kWh
WLLS1 | RTU16 | 2024-03-21 15:45:05 | Compressor run ignoring free cooling Opportunity of 8.35 kWh
WLLS1 | RTU16 | 2024-03-25 16:00:04 | Compressor run ignoring free cooling Opportunity of 12.20 kWh
WLLS1 | RTU16 | 2024-05-14 07:00:04 | Compressor run ignoring free cooling Opportunity of 1.73 kWh
WLLS1 | RTU16 | 2024-05-31 20:45:00 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU17 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU17 | 2024-01-11 21:15:05 | Short Cycling Detected
WLLS1 | RTU17 | 2024-03-05 07:45:02 | Compressor run ignoring free cooling Opportunity of 7.14 kWh
WLLS1 | RTU17 | 2024-03-05 10:00:05 | Compressor run ignoring free cooling Opportunity of 7.19 kWh
WLLS1 | RTU17 | 2024-03-05 10:15:00 | Compressor run ignoring free cooling Opportunity of 7.26 kWh
WLLS1 | RTU17 | 2024-03-05 12:30:02 | Compressor run ignoring free cooling Opportunity of 7.32 kWh
WLLS1 | RTU17 | 2024-03-05 15:15:00 | Compressor run ignoring free cooling Opportunity of 7.11 kWh
WLLS1 | RTU17 | 2024-03-05 17:30:05 | Compressor run ignoring free cooling Opportunity of 6.89 kWh
WLLS1 | RTU17 | 2024-03-05 17:45:00 | Compressor run ignoring free cooling Opportunity of 6.84 kWh
WLLS1 | RTU17 | 2024-03-05 20:00:02 | Compressor run ignoring free cooling Opportunity of 6.70 kWh
WLLS1 | RTU17 | 2024-03-05 22:30:03 | Compressor run ignoring free cooling Opportunity of 6.43 kWh
WLLS1 | RTU17 | 2024-03-05 22:44:59 | Compressor run ignoring free cooling Opportunity of 6.49 kWh
WLLS1 | RTU17 | 2024-03-05 22:59:58 | Compressor run ignoring free cooling Opportunity of 6.41 kWh
WLLS1 | RTU17 | 2024-03-07 22:30:03 | Compressor run ignoring free cooling Opportunity of 4.72 kWh
WLLS1 | RTU17 | 2024-03-08 06:15:05 | Compressor run ignoring free cooling Opportunity of 4.42 kWh
WLLS1 | RTU17 | 2024-03-08 06:30:00 | Compressor run ignoring free cooling Opportunity of 4.41 kWh
WLLS1 | RTU17 | 2024-03-08 08:45:02 | Compressor run ignoring free cooling Opportunity of 4.62 kWh
WLLS1 | RTU17 | 2024-03-08 11:00:05 | Compressor run ignoring free cooling Opportunity of 7.35 kWh
WLLS1 | RTU17 | 2024-03-08 11:15:00 | Compressor run ignoring free cooling Opportunity of 7.35 kWh
WLLS1 | RTU17 | 2024-03-08 13:45:02 | Compressor run ignoring free cooling Opportunity of 7.34 kWh
WLLS1 | RTU17 | 2024-03-08 13:59:58 | Compressor run ignoring free cooling Opportunity of 7.42 kWh
WLLS1 | RTU17 | 2024-03-08 14:14:57 | Compressor run ignoring free cooling Opportunity of 7.39 kWh
WLLS1 | RTU17 | 2024-03-08 16:30:05 | Compressor run ignoring free cooling Opportunity of 6.96 kWh
WLLS1 | RTU17 | 2024-03-08 16:45:00 | Compressor run ignoring free cooling Opportunity of 6.97 kWh
WLLS1 | RTU17 | 2024-03-08 18:45:06 | Compressor run ignoring free cooling Opportunity of 6.60 kWh
WLLS1 | RTU17 | 2024-03-08 19:00:00 | Compressor run ignoring free cooling Opportunity of 6.55 kWh
WLLS1 | RTU17 | 2024-03-08 21:15:02 | Compressor run ignoring free cooling Opportunity of 6.49 kWh
WLLS1 | RTU17 | 2024-03-15 06:00:03 | Compressor run ignoring free cooling Opportunity of 7.33 kWh
WLLS1 | RTU17 | 2024-03-15 06:15:00 | Compressor run ignoring free cooling Opportunity of 7.30 kWh
WLLS1 | RTU17 | 2024-03-16 07:00:01 | Compressor run ignoring free cooling Opportunity of 7.32 kWh
WLLS1 | RTU17 | 2024-03-16 09:30:04 | Compressor run ignoring free cooling Opportunity of 7.32 kWh
WLLS1 | RTU17 | 2024-03-16 09:44:58 | Compressor run ignoring free cooling Opportunity of 7.40 kWh
WLLS1 | RTU17 | 2024-03-16 12:00:05 | Compressor run ignoring free heating Opportunity of 7.44 kWh
WLLS1 | RTU18 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU18 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU18 | 2024-05-23 22:14:58 | Compressor run ignoring free cooling Opportunity of 4.87 kWh
WLLS1 | RTU18 | 2024-05-25 20:45:02 | Compressor run ignoring free cooling Opportunity of 4.78 kWh
WLLS1 | RTU18 | 2024-05-31 20:45:00 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU19 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU19 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU19 | 2024-03-19 07:59:56 | Compressor run ignoring free cooling Opportunity of 12.11 kWh
WLLS1 | RTU19 | 2024-03-19 08:44:45 | Compressor run ignoring free cooling Opportunity of 11.02 kWh
WLLS1 | RTU19 | 2024-05-06 22:14:55 | Compressor run ignoring free cooling Opportunity of 7.67 kWh
WLLS1 | RTU19 | 2024-05-09 05:14:47 | Compressor run ignoring free cooling Opportunity of 8.40 kWh
WLLS1 | RTU19 | 2024-05-09 05:29:55 | Compressor run ignoring free cooling Opportunity of 8.38 kWh
WLLS1 | RTU19 | 2024-05-24 05:44:46 | Compressor run ignoring free cooling Opportunity of 8.38 kWh
WLLS1 | RTU19 | 2024-05-24 19:59:53 | Compressor run ignoring free cooling Opportunity of 8.78 kWh
WLLS1 | RTU19 | 2024-05-24 20:14:57 | Compressor run ignoring free cooling Opportunity of 8.80 kWh
WLLS1 | RTU19 | 2024-05-24 20:30:01 | Compressor run ignoring free cooling Opportunity of 8.65 kWh
WLLS1 | RTU19 | 2024-05-25 20:45:02 | Compressor run ignoring free cooling Opportunity of 8.34 kWh
WLLS1 | RTU19 | 2024-05-27 05:14:52 | Compressor run ignoring free cooling Opportunity of 8.80 kWh
WLLS1 | RTU19 | 2024-05-27 05:29:57 | Compressor run ignoring free cooling Opportunity of 8.76 kWh
WLLS1 | RTU19 | 2024-05-31 19:44:47 | Compressor run ignoring free cooling Opportunity of 8.74 kWh
WLLS1 | RTU19 | 2024-05-31 19:59:52 | Compressor run ignoring free cooling Opportunity of 8.60 kWh
WLLS1 | RTU19 | 2024-03-30 11:44:44 | Compressor run ignoring free heating Opportunity of 9.20 kWh
WLLS1 | RTU19 | 2024-04-08 10:29:53 | Compressor run ignoring free heating Opportunity of 9.11 kWh
WLLS1 | RTU19 | 2024-04-08 10:44:57 | Compressor run ignoring free heating Opportunity of 9.22 kWh
WLLS1 | RTU19 | 2024-04-08 11:00:02 | Compressor run ignoring free heating Opportunity of 9.38 kWh
WLLS1 | RTU19 | 2024-04-23 11:44:48 | Compressor run ignoring free heating Opportunity of 8.60 kWh
WLLS1 | RTU19 | 2024-04-23 12:59:47 | Compressor run ignoring free heating Opportunity of 8.65 kWh
WLLS1 | RTU19 | 2024-04-23 14:14:45 | Compressor run ignoring free heating Opportunity of 8.56 kWh
WLLS1 | RTU19 | 2024-04-24 10:59:48 | Compressor run ignoring free heating Opportunity of 10.20 kWh
WLLS1 | RTU19 | 2024-04-25 11:14:44 | Compressor run ignoring free heating Opportunity of 10.18 kWh
WLLS1 | RTU19 | 2024-04-25 11:29:53 | Compressor run ignoring free heating Opportunity of 10.22 kWh
WLLS1 | RTU20 | 2024-01-16 21:45:00 | Unit Quick ON/Off within 15 min
WLLS1 | RTU20 | 2024-03-24 05:29:54 | Unit Quick ON/Off within 15 min
WLLS1 | RTU20 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU20 | 2024-04-08 11:00:02 | No findings on Compressor being run ignoring free cooling Opportunity
WLLS1 | RTU20 | 2024-04-08 11:00:02 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU21 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU21 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU21 | 2024-03-18 13:14:51 | No findings on Compressor being run ignoring free cooling Opportunity
WLLS1 | RTU21 | 2024-03-18 13:14:51 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU22 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU22 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU22 | 2024-05-31 23:14:46 | No findings on Compressor being run ignoring free cooling Opportunity
WLLS1 | RTU22 | 2024-05-31 23:14:46 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU25 | 2024-01-05 12:15:00 | Unit Quick ON/Off within 15 min
WLLS1 | RTU25 | 2024-01-11 09:44:52 | Unit Quick ON/Off within 15 min
WLLS1 | RTU25 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU25 | 2024-03-05 15:15:00 | Compressor run ignoring free cooling Opportunity of 5.19 kWh
WLLS1 | RTU25 | 2024-03-05 15:29:56 | Compressor run ignoring free cooling Opportunity of 5.20 kWh
WLLS1 | RTU25 | 2024-03-05 15:44:50 | Compressor run ignoring free cooling Opportunity of 5.19 kWh
WLLS1 | RTU25 | 2024-03-05 17:30:04 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU25 | 2024-03-05 17:44:59 | Compressor run ignoring free cooling Opportunity of 5.10 kWh
WLLS1 | RTU25 | 2024-03-05 17:59:54 | Compressor run ignoring free cooling Opportunity of 5.09 kWh
WLLS1 | RTU25 | 2024-03-05 20:00:02 | Compressor run ignoring free cooling Opportunity of 5.15 kWh
WLLS1 | RTU25 | 2024-03-05 20:14:57 | Compressor run ignoring free cooling Opportunity of 5.13 kWh
WLLS1 | RTU25 | 2024-03-05 20:29:54 | Compressor run ignoring free cooling Opportunity of 5.11 kWh
WLLS1 | RTU25 | 2024-03-08 14:14:57 | Compressor run ignoring free cooling Opportunity of 5.25 kWh
WLLS1 | RTU25 | 2024-03-08 14:29:54 | Compressor run ignoring free cooling Opportunity of 5.24 kWh
WLLS1 | RTU25 | 2024-03-08 16:30:04 | Compressor run ignoring free cooling Opportunity of 5.15 kWh
WLLS1 | RTU25 | 2024-03-08 16:44:59 | Compressor run ignoring free cooling Opportunity of 5.20 kWh
WLLS1 | RTU25 | 2024-03-08 16:59:55 | Compressor run ignoring free cooling Opportunity of 5.14 kWh
WLLS1 | RTU25 | 2024-03-08 17:14:50 | Compressor run ignoring free cooling Opportunity of 5.12 kWh
WLLS1 | RTU25 | 2024-03-08 18:45:06 | Compressor run ignoring free cooling Opportunity of 5.05 kWh
WLLS1 | RTU25 | 2024-03-08 19:00:00 | Compressor run ignoring free cooling Opportunity of 5.01 kWh
WLLS1 | RTU25 | 2024-03-08 19:14:55 | Compressor run ignoring free cooling Opportunity of 5.01 kWh
WLLS1 | RTU25 | 2024-03-18 13:29:47 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU27 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU27 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU27 | 2024-03-04 15:15:04 | Compressor run ignoring free cooling Opportunity of 9.69 kWh
WLLS1 | RTU27 | 2024-05-23 22:14:57 | Compressor run ignoring free cooling Opportunity of 9.69 kWh
WLLS1 | RTU27 | 2024-05-23 22:30:01 | Compressor run ignoring free cooling Opportunity of 9.69 kWh
WLLS1 | RTU27 | 2024-05-24 22:44:52 | Compressor run ignoring free cooling Opportunity of 9.76 kWh
WLLS1 | RTU27 | 2024-05-27 05:14:52 | Compressor run ignoring free cooling Opportunity of 9.58 kWh
WLLS1 | RTU27 | 2024-05-27 08:44:54 | Compressor run ignoring free cooling Opportunity of 9.69 kWh
WLLS1 | RTU27 | 2024-05-29 20:44:57 | Compressor run ignoring free cooling Opportunity of 9.98 kWh
WLLS1 | RTU27 | 2024-05-31 20:44:59 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU28 | 2024-01-04 11:29:58 | Unit Quick ON/Off within 15 min
WLLS1 | RTU28 | 2024-01-08 09:45:00 | Unit Quick ON/Off within 15 min
WLLS1 | RTU28 | 2024-01-15 11:30:01 | Unit Quick ON/Off within 15 min
WLLS1 | RTU28 | 2024-01-16 10:14:52 | Unit Quick ON/Off within 15 min
WLLS1 | RTU28 | 2024-01-17 13:59:59 | Unit Quick ON/Off within 15 min
WLLS1 | RTU28 | 2024-02-06 14:30:01 | Unit Quick ON/Off within 15 min
WLLS1 | RTU28 | 2024-03-04 12:59:59 | Unit Quick ON/Off within 15 min
WLLS1 | RTU28 | 2024-03-05 12:44:56 | Unit Quick ON/Off within 15 min
WLLS1 | RTU28 | 2024-03-19 12:14:51 | Unit Quick ON/Off within 15 min
WLLS1 | RTU28 | 2024-03-26 11:14:59 | Unit Quick ON/Off within 15 min
WLLS1 | RTU28 | 2024-03-26 15:30:00 | Unit Quick ON/Off within 15 min
WLLS1 | RTU28 | 2024-04-08 11:00:02 | Unit Quick ON/Off within 15 min
WLLS1 | RTU28 | 2024-05-13 14:14:59 | Unit Quick ON/Off within 15 min
WLLS1 | RTU28 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU28 | 2024-01-04 11:44:54 | Compressor run ignoring free cooling Opportunity of 2.26 kWh
WLLS1 | RTU28 | 2024-01-04 13:45:04 | Compressor run ignoring free cooling Opportunity of 2.20 kWh
WLLS1 | RTU28 | 2024-01-08 12:45:00 | Compressor run ignoring free cooling Opportunity of 2.24 kWh
WLLS1 | RTU28 | 2024-01-15 08:59:57 | Compressor run ignoring free cooling Opportunity of 2.22 kWh
WLLS1 | RTU28 | 2024-01-15 09:14:58 | Compressor run ignoring free cooling Opportunity of 2.21 kWh
WLLS1 | RTU28 | 2024-01-15 09:59:59 | Compressor run ignoring free cooling Opportunity of 2.19 kWh
WLLS1 | RTU28 | 2024-01-15 10:15:00 | Compressor run ignoring free cooling Opportunity of 2.22 kWh
WLLS1 | RTU28 | 2024-01-15 10:30:00 | Compressor run ignoring free cooling Opportunity of 2.24 kWh
WLLS1 | RTU28 | 2024-01-15 10:45:01 | Compressor run ignoring free cooling Opportunity of 2.21 kWh
WLLS1 | RTU28 | 2024-01-15 11:45:01 | Compressor run ignoring free cooling Opportunity of 2.29 kWh
WLLS1 | RTU28 | 2024-01-15 12:00:01 | Compressor run ignoring free cooling Opportunity of 2.29 kWh
WLLS1 | RTU28 | 2024-01-16 09:44:53 | Compressor run ignoring free cooling Opportunity of 2.26 kWh
WLLS1 | RTU28 | 2024-01-22 12:00:04 | Compressor run ignoring free cooling Opportunity of 2.17 kWh
WLLS1 | RTU28 | 2024-01-22 13:00:04 | Compressor run ignoring free cooling Opportunity of 2.20 kWh
WLLS1 | RTU28 | 2024-02-06 13:59:52 | Compressor run ignoring free cooling Opportunity of 2.23 kWh
WLLS1 | RTU28 | 2024-02-20 10:00:04 | Compressor run ignoring free cooling Opportunity of 2.20 kWh
WLLS1 | RTU28 | 2024-02-20 13:30:06 | Compressor run ignoring free cooling Opportunity of 2.30 kWh
WLLS1 | RTU28 | 2024-02-26 11:30:04 | Compressor run ignoring free cooling Opportunity of 2.27 kWh
WLLS1 | RTU28 | 2024-03-19 11:15:05 | Compressor run ignoring free cooling Opportunity of 2.20 kWh
WLLS1 | RTU28 | 2024-03-19 11:30:01 | Compressor run ignoring free cooling Opportunity of 2.20 kWh
WLLS1 | RTU28 | 2024-03-19 11:44:57 | Compressor run ignoring free cooling Opportunity of 2.23 kWh
WLLS1 | RTU28 | 2024-03-26 11:29:56 | Compressor run ignoring free cooling Opportunity of 2.24 kWh
WLLS1 | RTU28 | 2024-03-26 15:44:56 | Compressor run ignoring free cooling Opportunity of 2.32 kWh
WLLS1 | RTU28 | 2024-04-22 13:59:54 | Compressor run ignoring free cooling Opportunity of 2.27 kWh
WLLS1 | RTU28 | 2024-04-23 10:44:55 | Compressor run ignoring free cooling Opportunity of 2.27 kWh
WLLS1 | RTU28 | 2024-05-14 08:59:54 | Compressor run ignoring free cooling Opportunity of 2.35 kWh
WLLS1 | RTU28 | 2024-05-31 20:44:59 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU29 | 2024-04-04 14:30:00 | Unit Quick ON/Off within 15 min
WLLS1 | RTU29 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU29 | 2024-04-01 20:59:57 | Compressor run ignoring free cooling Opportunity of 8.39 kWh
WLLS1 | RTU29 | 2024-04-01 21:15:00 | Compressor run ignoring free cooling Opportunity of 3.41 kWh
WLLS1 | RTU29 | 2024-05-24 19:59:53 | Compressor run ignoring free cooling Opportunity of 3.39 kWh
WLLS1 | RTU29 | 2024-05-24 20:14:56 | Compressor run ignoring free cooling Opportunity of 8.08 kWh
WLLS1 | RTU29 | 2024-05-29 20:44:57 | Compressor run ignoring free cooling Opportunity of 8.04 kWh
WLLS1 | RTU29 | 2024-03-05 14:45:05 | Compressor run ignoring free heating Opportunity of 2.66 kWh
WLLS1 | RTU29 | 2024-03-30 11:59:47 | Compressor run ignoring free heating Opportunity of 2.66 kWh
WLLS1 | RTU29 | 2024-03-30 12:14:50 | Compressor run ignoring free heating Opportunity of 2.66 kWh
WLLS1 | RTU29 | 2024-04-19 19:59:54 | Compressor run ignoring free heating Opportunity of 8.08 kWh
WLLS1 | RTU29 | 2024-04-23 11:44:47 | Compressor run ignoring free heating Opportunity of 2.61 kWh
WLLS1 | RTU29 | 2024-04-29 16:14:55 | Compressor run ignoring free heating Opportunity of 8.33 kWh
WLLS1 | RTU29 | 2024-04-29 21:14:49 | Compressor run ignoring free heating Opportunity of 8.24 kWh
WLLS1 | RTU29 | 2024-04-30 21:29:49 | Compressor run ignoring free heating Opportunity of 8.24 kWh
WLLS1 | RTU29 | 2024-04-30 22:44:49 | Compressor run ignoring free heating Opportunity of 3.39 kWh
WLLS1 | RTU29 | 2024-05-07 15:14:49 | Compressor run ignoring free heating Opportunity of 8.17 kWh
WLLS1 | RTU29 | 2024-05-10 16:30:01 | Compressor run ignoring free heating Opportunity of 3.32 kWh
WLLS1 | RTU29 | 2024-05-10 16:44:53 | Compressor run ignoring free heating Opportunity of 3.32 kWh
WLLS1 | RTU29 | 2024-05-10 19:45:01 | Compressor run ignoring free heating Opportunity of 7.91 kWh
WLLS1 | RTU29 | 2024-05-16 17:14:53 | Compressor run ignoring free heating Opportunity of 8.22 kWh
WLLS1 | RTU29 | 2024-05-16 18:29:53 | Compressor run ignoring free heating Opportunity of 3.37 kWh
WLLS1 | RTU29 | 2024-05-21 15:59:47 | Compressor run ignoring free heating Opportunity of 8.26 kWh
WLLS1 | RTU29 | 2024-05-21 16:14:51 | Compressor run ignoring free heating Opportunity of 8.44 kWh
WLLS1 | RTU29 | 2024-05-21 16:29:55 | Compressor run ignoring free heating Opportunity of 8.39 kWh
WLLS1 | RTU29 | 2024-05-21 16:44:59 | Compressor run ignoring free heating Opportunity of 8.35 kWh
WLLS1 | RTU29 | 2024-05-21 18:59:46 | Compressor run ignoring free heating Opportunity of 8.26 kWh
WLLS1 | RTU29 | 2024-05-22 13:44:47 | Compressor run ignoring free heating Opportunity of 8.26 kWh
WLLS1 | RTU29 | 2024-05-22 13:59:49 | Compressor run ignoring free heating Opportunity of 8.31 kWh
WLLS1 | RTU29 | 2024-05-22 14:14:52 | Compressor run ignoring free heating Opportunity of 8.39 kWh
WLLS1 | RTU29 | 2024-05-22 14:29:56 | Compressor run ignoring free heating Opportunity of 8.28 kWh
WLLS1 | RTU29 | 2024-05-22 14:44:59 | Compressor run ignoring free heating Opportunity of 8.33 kWh
WLLS1 | RTU29 | 2024-05-23 11:59:49 | Compressor run ignoring free heating Opportunity of 8.51 kWh
WLLS1 | RTU29 | 2024-05-23 12:14:52 | Compressor run ignoring free heating Opportunity of 8.51 kWh
WLLS1 | RTU29 | 2024-05-23 12:29:55 | Compressor run ignoring free heating Opportunity of 8.48 kWh
WLLS1 | RTU29 | 2024-05-24 16:29:51 | Compressor run ignoring free heating Opportunity of 3.39 kWh
WLLS1 | RTU29 | 2024-05-24 16:44:54 | Compressor run ignoring free heating Opportunity of 5.58 kWh
WLLS1 | RTU29 | 2024-05-24 22:14:45 | Compressor run ignoring free heating Opportunity of 7.97 kWh
WLLS1 | RTU29 | 2024-05-24 22:29:49 | Compressor run ignoring free heating Opportunity of 7.95 kWh
WLLS1 | RTU29 | 2024-05-24 22:44:51 | Compressor run ignoring free heating Opportunity of 7.93 kWh
WLLS1 | RTU29 | 2024-05-26 15:29:46 | Compressor run ignoring free heating Opportunity of 8.59 kWh
WLLS1 | RTU29 | 2024-05-26 15:44:49 | Compressor run ignoring free heating Opportunity of 8.53 kWh
WLLS1 | RTU29 | 2024-05-26 15:59:51 | Compressor run ignoring free heating Opportunity of 8.59 kWh
WLLS1 | RTU29 | 2024-05-26 16:14:57 | Compressor run ignoring free heating Opportunity of 8.51 kWh
WLLS1 | RTU29 | 2024-05-29 13:14:55 | Compressor run ignoring free heating Opportunity of 8.26 kWh
WLLS1 | RTU29 | 2024-05-29 16:14:46 | Compressor run ignoring free heating Opportunity of 8.33 kWh
WLLS1 | RTU29 | 2024-05-29 16:29:50 | Compressor run ignoring free heating Opportunity of 8.35 kWh
WLLS1 | RTU29 | 2024-05-29 16:44:53 | Compressor run ignoring free heating Opportunity of 8.37 kWh
WLLS1 | RTU29 | 2024-05-29 16:59:55 | Compressor run ignoring free heating Opportunity of 8.35 kWh
WLLS1 | RTU29 | 2024-05-29 17:14:59 | Compressor run ignoring free heating Opportunity of 8.33 kWh
WLLS1 | RTU29 | 2024-05-31 16:44:57 | Compressor run ignoring free heating Opportunity of 7.93 kWh
WLLS1 | RTU29 | 2024-05-31 19:44:47 | Compressor run ignoring free heating Opportunity of 8.06 kWh
WLLS1 | RTU3 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU3 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU3 | 2024-04-19 19:44:41 | Compressor run ignoring free cooling Opportunity of 4.88 kWh
WLLS1 | RTU3 | 2024-05-14 09:44:46 | Compressor run ignoring free cooling Opportunity of 4.94 kWh
WLLS1 | RTU3 | 2024-05-14 17:29:55 | Compressor run ignoring free cooling Opportunity of 1.54 kWh
WLLS1 | RTU3 | 2024-05-25 19:44:42 | Compressor run ignoring free cooling Opportunity of 4.77 kWh
WLLS1 | RTU3 | 2024-05-29 20:44:54 | Compressor run ignoring free cooling Opportunity of 5.12 kWh
WLLS1 | RTU3 | 2024-05-31 23:14:42 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU30 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU30 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU30 | 2024-05-04 06:15:00 | Compressor run ignoring free cooling Opportunity of 2.79 kWh
WLLS1 | RTU30 | 2024-05-04 09:45:03 | Compressor run ignoring free cooling Opportunity of 2.79 kWh
WLLS1 | RTU30 | 2024-05-04 22:30:04 | Compressor run ignoring free cooling Opportunity of 2.81 kWh
WLLS1 | RTU30 | 2024-05-04 23:15:01 | Compressor run ignoring free cooling Opportunity of 2.81 kWh
WLLS1 | RTU30 | 2024-05-06 20:44:44 | Compressor run ignoring free cooling Opportunity of 2.77 kWh
WLLS1 | RTU30 | 2024-05-06 20:59:54 | Compressor run ignoring free cooling Opportunity of 2.77 kWh
WLLS1 | RTU30 | 2024-05-06 22:14:54 | Compressor run ignoring free cooling Opportunity of 2.79 kWh
WLLS1 | RTU30 | 2024-05-06 23:14:44 | Compressor run ignoring free cooling Opportunity of 2.79 kWh
WLLS1 | RTU30 | 2024-05-09 06:44:47 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU30 | 2024-05-18 17:44:46 | Compressor run ignoring free cooling Opportunity of 9.95 kWh
WLLS1 | RTU30 | 2024-05-24 05:44:45 | Compressor run ignoring free cooling Opportunity of 2.74 kWh
WLLS1 | RTU30 | 2024-05-24 05:59:48 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU30 | 2024-05-24 06:14:53 | Compressor run ignoring free cooling Opportunity of 2.74 kWh
WLLS1 | RTU30 | 2024-05-24 06:29:55 | Compressor run ignoring free cooling Opportunity of 2.74 kWh
WLLS1 | RTU30 | 2024-05-24 08:59:43 | Compressor run ignoring free heating Opportunity of 2.70 kWh
WLLS1 | RTU31 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU31 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU31 | 2024-05-10 19:15:04 | Compressor run ignoring free cooling Opportunity of 17.64 kWh
WLLS1 | RTU31 | 2024-05-10 21:00:01 | Compressor run ignoring free cooling Opportunity of 17.46 kWh
WLLS1 | RTU31 | 2024-05-10 22:30:07 | Compressor run ignoring free cooling Opportunity of 17.24 kWh
WLLS1 | RTU31 | 2024-05-15 22:30:08 | Compressor run ignoring free cooling Opportunity of 18.18 kWh
WLLS1 | RTU31 | 2024-05-15 22:45:07 | Compressor run ignoring free cooling Opportunity of 18.00 kWh
WLLS1 | RTU31 | 2024-05-15 23:00:05 | Compressor run ignoring free cooling Opportunity of 18.00 kWh
WLLS1 | RTU31 | 2024-05-15 23:15:04 | Compressor run ignoring free cooling Opportunity of 18.04 kWh
WLLS1 | RTU31 | 2024-05-16 21:14:54 | Compressor run ignoring free cooling Opportunity of 18.18 kWh
WLLS1 | RTU31 | 2024-05-16 22:29:56 | Compressor run ignoring free cooling Opportunity of 17.86 kWh
WLLS1 | RTU31 | 2024-05-17 20:14:54 | Compressor run ignoring free cooling Opportunity of 18.22 kWh
WLLS1 | RTU31 | 2024-05-17 21:44:57 | Compressor run ignoring free cooling Opportunity of 18.13 kWh
WLLS1 | RTU31 | 2024-05-18 18:14:54 | Compressor run ignoring free cooling Opportunity of 18.58 kWh
WLLS1 | RTU31 | 2024-05-20 20:29:56 | Compressor run ignoring free cooling Opportunity of 18.40 kWh
WLLS1 | RTU31 | 2024-05-20 21:44:57 | Compressor run ignoring free cooling Opportunity of 18.31 kWh
WLLS1 | RTU31 | 2024-05-20 22:59:58 | Compressor run ignoring free cooling Opportunity of 18.22 kWh
WLLS1 | RTU31 | 2024-05-21 20:29:56 | Compressor run ignoring free cooling Opportunity of 18.45 kWh
WLLS1 | RTU31 | 2024-05-21 20:44:59 | Compressor run ignoring free cooling Opportunity of 18.45 kWh
WLLS1 | RTU31 | 2024-05-21 21:00:02 | Compressor run ignoring free cooling Opportunity of 18.31 kWh
WLLS1 | RTU31 | 2024-05-22 05:59:59 | Compressor run ignoring free cooling Opportunity of 17.15 kWh
WLLS1 | RTU31 | 2024-05-22 21:44:59 | Compressor run ignoring free cooling Opportunity of 18.62 kWh
WLLS1 | RTU31 | 2024-05-22 22:00:03 | Compressor run ignoring free cooling Opportunity of 18.62 kWh
WLLS1 | RTU31 | 2024-05-23 20:14:59 | Compressor run ignoring free cooling Opportunity of 18.27 kWh
WLLS1 | RTU31 | 2024-05-23 22:59:56 | Compressor run ignoring free cooling Opportunity of 18.40 kWh
WLLS1 | RTU31 | 2024-05-23 23:14:59 | Compressor run ignoring free cooling Opportunity of 18.45 kWh
WLLS1 | RTU31 | 2024-05-24 07:14:56 | Compressor run ignoring free cooling Opportunity of 18.22 kWh
WLLS1 | RTU31 | 2024-05-24 07:29:59 | Compressor run ignoring free cooling Opportunity of 17.91 kWh
WLLS1 | RTU31 | 2024-05-24 07:45:04 | Compressor run ignoring free cooling Opportunity of 18.22 kWh
WLLS1 | RTU31 | 2024-05-24 08:00:06 | Compressor run ignoring free cooling Opportunity of 18.22 kWh
WLLS1 | RTU31 | 2024-05-24 17:44:54 | Compressor run ignoring free cooling Opportunity of 18.58 kWh
WLLS1 | RTU31 | 2024-05-24 20:59:57 | Compressor run ignoring free cooling Opportunity of 18.54 kWh
WLLS1 | RTU31 | 2024-05-24 21:15:02 | Compressor run ignoring free cooling Opportunity of 18.18 kWh
WLLS1 | RTU31 | 2024-05-25 17:59:54 | Compressor run ignoring free cooling Opportunity of 18.13 kWh
WLLS1 | RTU31 | 2024-05-25 18:14:57 | Compressor run ignoring free cooling Opportunity of 17.82 kWh
WLLS1 | RTU31 | 2024-05-25 18:30:01 | Compressor run ignoring free cooling Opportunity of 17.73 kWh
WLLS1 | RTU31 | 2024-05-25 21:14:55 | Compressor run ignoring free cooling Opportunity of 18.09 kWh
WLLS1 | RTU31 | 2024-05-25 21:29:59 | Compressor run ignoring free cooling Opportunity of 18.13 kWh
WLLS1 | RTU31 | 2024-05-25 21:45:02 | Compressor run ignoring free cooling Opportunity of 18.04 kWh
WLLS1 | RTU31 | 2024-05-25 22:00:05 | Compressor run ignoring free cooling Opportunity of 17.95 kWh
WLLS1 | RTU31 | 2024-05-27 06:14:54 | Compressor run ignoring free cooling Opportunity of 18.22 kWh
WLLS1 | RTU31 | 2024-05-27 06:29:56 | Compressor run ignoring free cooling Opportunity of 18.27 kWh
WLLS1 | RTU31 | 2024-05-27 06:45:00 | Compressor run ignoring free cooling Opportunity of 18.13 kWh
WLLS1 | RTU31 | 2024-05-29 21:14:54 | Compressor run ignoring free cooling Opportunity of 18.89 kWh
WLLS1 | RTU31 | 2024-05-29 21:29:57 | Compressor run ignoring free cooling Opportunity of 18.85 kWh
WLLS1 | RTU31 | 2024-05-29 21:45:00 | Compressor run ignoring free cooling Opportunity of 18.85 kWh
WLLS1 | RTU31 | 2024-05-29 22:00:02 | Compressor run ignoring free cooling Opportunity of 18.85 kWh
WLLS1 | RTU31 | 2024-05-29 22:15:05 | Compressor run ignoring free cooling Opportunity of 18.67 kWh
WLLS1 | RTU31 | 2024-05-30 07:00:02 | Compressor run ignoring free cooling Opportunity of 17.24 kWh
WLLS1 | RTU31 | 2024-05-30 20:14:57 | Compressor run ignoring free cooling Opportunity of 17.73 kWh
WLLS1 | RTU31 | 2024-05-30 20:30:00 | Compressor run ignoring free cooling Opportunity of 17.68 kWh
WLLS1 | RTU31 | 2024-05-30 20:45:03 | Compressor run ignoring free cooling Opportunity of 17.51 kWh
WLLS1 | RTU31 | 2024-05-31 21:14:57 | Compressor run ignoring free cooling Opportunity of 18.22 kWh
WLLS1 | RTU31 | 2024-05-31 21:29:59 | Compressor run ignoring free cooling Opportunity of 18.09 kWh
WLLS1 | RTU31 | 2024-05-31 21:45:02 | Compressor run ignoring free cooling Opportunity of 18.09 kWh
WLLS1 | RTU31 | 2024-04-01 17:44:53 | Compressor run ignoring free heating Opportunity of 7.92 kWh
WLLS1 | RTU31 | 2024-04-01 17:59:55 | Compressor run ignoring free heating Opportunity of 7.88 kWh
WLLS1 | RTU31 | 2024-04-01 18:14:58 | Compressor run ignoring free heating Opportunity of 8.01 kWh
WLLS1 | RTU31 | 2024-04-01 18:30:00 | Compressor run ignoring free heating Opportunity of 8.10 kWh
WLLS1 | RTU31 | 2024-04-01 18:45:04 | Compressor run ignoring free heating Opportunity of 8.06 kWh
WLLS1 | RTU31 | 2024-04-01 21:44:56 | Compressor run ignoring free heating Opportunity of 8.01 kWh
WLLS1 | RTU31 | 2024-04-01 22:00:00 | Compressor run ignoring free heating Opportunity of 8.06 kWh
WLLS1 | RTU31 | 2024-04-01 22:15:05 | Compressor run ignoring free heating Opportunity of 7.97 kWh
WLLS1 | RTU31 | 2024-04-02 13:45:03 | Compressor run ignoring free heating Opportunity of 7.92 kWh
WLLS1 | RTU31 | 2024-04-02 16:29:57 | Compressor run ignoring free heating Opportunity of 7.92 kWh
WLLS1 | RTU31 | 2024-04-02 16:45:00 | Compressor run ignoring free heating Opportunity of 7.97 kWh
WLLS1 | RTU31 | 2024-04-02 19:44:53 | Compressor run ignoring free heating Opportunity of 7.88 kWh
WLLS1 | RTU31 | 2024-04-02 19:59:57 | Compressor run ignoring free heating Opportunity of 8.06 kWh
WLLS1 | RTU31 | 2024-04-02 20:15:01 | Compressor run ignoring free heating Opportunity of 8.01 kWh
WLLS1 | RTU31 | 2024-04-02 20:30:04 | Compressor run ignoring free heating Opportunity of 8.06 kWh
WLLS1 | RTU31 | 2024-04-02 23:14:54 | Compressor run ignoring free heating Opportunity of 7.97 kWh
WLLS1 | RTU31 | 2024-04-19 15:14:52 | Compressor run ignoring free heating Opportunity of 8.06 kWh
WLLS1 | RTU31 | 2024-04-19 15:30:00 | Compressor run ignoring free heating Opportunity of 8.06 kWh
WLLS1 | RTU31 | 2024-04-19 17:44:54 | Compressor run ignoring free heating Opportunity of 8.01 kWh
WLLS1 | RTU31 | 2024-04-19 18:59:53 | Compressor run ignoring free heating Opportunity of 8.01 kWh
WLLS1 | RTU31 | 2024-04-29 19:14:56 | Compressor run ignoring free heating Opportunity of 7.92 kWh
WLLS1 | RTU31 | 2024-04-29 20:29:56 | Compressor run ignoring free heating Opportunity of 8.01 kWh
WLLS1 | RTU31 | 2024-04-29 21:44:55 | Compressor run ignoring free heating Opportunity of 7.97 kWh
WLLS1 | RTU31 | 2024-04-29 22:59:55 | Compressor run ignoring free heating Opportunity of 8.10 kWh
WLLS1 | RTU31 | 2024-04-30 15:44:52 | Compressor run ignoring free heating Opportunity of 7.88 kWh
WLLS1 | RTU31 | 2024-04-30 16:00:00 | Compressor run ignoring free heating Opportunity of 7.79 kWh
WLLS1 | RTU31 | 2024-04-30 17:15:01 | Compressor run ignoring free heating Opportunity of 7.97 kWh
WLLS1 | RTU31 | 2024-04-30 19:29:53 | Compressor run ignoring free heating Opportunity of 8.06 kWh
WLLS1 | RTU31 | 2024-04-30 20:44:54 | Compressor run ignoring free heating Opportunity of 7.92 kWh
WLLS1 | RTU31 | 2024-04-30 21:59:58 | Compressor run ignoring free heating Opportunity of 8.06 kWh
WLLS1 | RTU31 | 2024-04-30 23:14:55 | Compressor run ignoring free heating Opportunity of 8.10 kWh
WLLS1 | RTU31 | 2024-05-01 12:29:53 | Compressor run ignoring free heating Opportunity of 7.92 kWh
WLLS1 | RTU31 | 2024-05-01 13:59:55 | Compressor run ignoring free heating Opportunity of 7.92 kWh
WLLS1 | RTU31 | 2024-05-06 18:44:50 | Compressor run ignoring free heating Opportunity of 8.10 kWh
WLLS1 | RTU31 | 2024-05-07 11:59:52 | Compressor run ignoring free heating Opportunity of 7.92 kWh
WLLS1 | RTU31 | 2024-05-07 14:29:53 | Compressor run ignoring free heating Opportunity of 7.88 kWh
WLLS1 | RTU31 | 2024-05-07 15:44:56 | Compressor run ignoring free heating Opportunity of 7.79 kWh
WLLS1 | RTU31 | 2024-05-07 16:00:06 | Compressor run ignoring free heating Opportunity of 7.84 kWh
WLLS1 | RTU31 | 2024-05-08 15:14:58 | Compressor run ignoring free heating Opportunity of 7.84 kWh
WLLS1 | RTU31 | 2024-05-08 16:29:55 | Compressor run ignoring free heating Opportunity of 7.84 kWh
WLLS1 | RTU31 | 2024-05-08 17:44:55 | Compressor run ignoring free heating Opportunity of 7.84 kWh
WLLS1 | RTU31 | 2024-05-08 18:59:52 | Compressor run ignoring free heating Opportunity of 7.97 kWh
WLLS1 | RTU31 | 2024-05-08 22:59:53 | Compressor run ignoring free heating Opportunity of 7.97 kWh
WLLS1 | RTU32 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU32 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU32 | 2024-01-01 08:00:07 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-02 06:15:06 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-02 06:30:00 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-02 06:44:55 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-02 06:59:49 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-03 06:15:10 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-03 06:30:04 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-03 06:44:58 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-03 06:59:52 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-03 07:14:49 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-03 07:29:47 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-05 05:45:05 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-05 06:00:01 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-05 06:14:55 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-05 06:29:51 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-05 06:44:49 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-05 08:15:08 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-05 08:30:02 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-05 08:44:56 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-05 08:59:51 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-05 22:45:05 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-05 23:00:00 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-05 23:14:56 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-08 08:15:06 | Compressor run ignoring free cooling Opportunity of 2.81 kWh
WLLS1 | RTU32 | 2024-01-08 08:30:02 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-08 08:44:56 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-08 18:30:06 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-08 18:45:01 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-08 18:59:56 | Compressor run ignoring free cooling Opportunity of 2.83 kWh
WLLS1 | RTU32 | 2024-01-08 19:14:53 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-08 21:00:07 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-08 21:15:01 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-08 21:29:58 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-08 21:44:53 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-08 21:59:50 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-11 05:14:46 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-11 07:00:06 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-11 07:15:02 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-11 07:29:59 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-11 07:44:56 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-11 07:59:51 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-11 08:14:49 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-11 08:29:46 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-12 06:59:46 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-12 07:14:47 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-12 07:29:48 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-12 07:44:47 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-12 07:59:49 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-12 08:14:50 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-12 08:29:50 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-14 05:15:05 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-14 05:30:07 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-16 07:30:08 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-17 05:14:54 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-17 05:29:56 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-17 05:44:57 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-17 05:59:57 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU32 | 2024-01-17 06:14:58 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-17 06:29:59 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-17 06:44:59 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-17 07:00:02 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU32 | 2024-01-17 07:15:03 | Compressor run ignoring free cooling Opportunity of 2.92 kWh
WLLS1 | RTU32 | 2024-01-17 07:30:03 | Compressor run ignoring free cooling Opportunity of 2.74 kWh
WLLS1 | RTU32 | 2024-01-17 07:45:04 | Compressor run ignoring free cooling Opportunity of 2.74 kWh
WLLS1 | RTU32 | 2024-01-17 08:00:04 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU32 | 2024-01-17 08:15:04 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-17 08:30:01 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-17 08:44:54 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-17 08:59:49 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-17 10:30:03 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-17 10:44:59 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-17 10:59:53 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-17 12:30:06 | Compressor run ignoring free cooling Opportunity of 2.83 kWh
WLLS1 | RTU32 | 2024-01-17 12:45:02 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-17 12:59:57 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-17 13:14:49 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-17 14:45:06 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-17 14:59:59 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-17 15:14:53 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-17 16:45:06 | Compressor run ignoring free cooling Opportunity of 2.58 kWh
WLLS1 | RTU32 | 2024-01-17 17:00:00 | Compressor run ignoring free cooling Opportunity of 2.56 kWh
WLLS1 | RTU32 | 2024-01-17 17:14:55 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-17 17:29:49 | Compressor run ignoring free cooling Opportunity of 2.56 kWh
WLLS1 | RTU32 | 2024-01-17 18:45:08 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-17 19:00:01 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-17 19:14:55 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-17 19:29:50 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-17 20:30:08 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-17 20:45:02 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-17 20:59:56 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-17 21:14:52 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-17 22:30:05 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-17 22:44:59 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-17 22:59:55 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-18 06:45:06 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-18 07:30:07 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-18 07:45:02 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-18 07:59:56 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU32 | 2024-01-18 08:14:51 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU32 | 2024-01-20 09:44:45 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-20 09:59:46 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-20 10:14:45 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-20 10:29:45 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-20 10:44:46 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-20 10:59:46 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-20 11:14:46 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-20 11:29:47 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-20 11:44:48 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-20 11:59:49 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-20 12:14:49 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-20 12:29:50 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-20 12:44:52 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-20 12:59:56 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-20 13:14:57 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-20 13:30:00 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-20 13:45:00 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-20 14:00:01 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-20 14:15:03 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-20 14:30:03 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-01-20 14:45:05 | Compressor run ignoring free cooling Opportunity of 2.83 kWh
WLLS1 | RTU32 | 2024-01-20 15:00:06 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-21 08:29:44 | Compressor run ignoring free cooling Opportunity of 2.76 kWh
WLLS1 | RTU32 | 2024-01-21 08:44:46 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-21 08:59:46 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-21 09:14:46 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-21 09:29:46 | Compressor run ignoring free cooling Opportunity of 2.74 kWh
WLLS1 | RTU32 | 2024-01-21 09:44:47 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-21 09:59:48 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-21 10:14:49 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU32 | 2024-01-21 10:29:48 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU32 | 2024-01-21 10:44:50 | Compressor run ignoring free cooling Opportunity of 2.74 kWh
WLLS1 | RTU32 | 2024-01-21 10:59:51 | Compressor run ignoring free cooling Opportunity of 2.74 kWh
WLLS1 | RTU32 | 2024-01-21 11:14:54 | Compressor run ignoring free cooling Opportunity of 2.76 kWh
WLLS1 | RTU32 | 2024-01-21 11:29:56 | Compressor run ignoring free cooling Opportunity of 2.90 kWh
WLLS1 | RTU32 | 2024-01-21 11:44:58 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-21 12:00:00 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU32 | 2024-01-21 12:15:03 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-21 12:30:04 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-21 12:45:05 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-21 13:00:05 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU32 | 2024-01-21 22:29:55 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-21 22:44:55 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-21 22:59:56 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-21 23:14:56 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-22 07:29:47 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-22 07:44:47 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-22 07:59:48 | Compressor run ignoring free cooling Opportunity of 2.74 kWh
WLLS1 | RTU32 | 2024-01-22 08:14:47 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-22 08:29:48 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU32 | 2024-01-22 08:44:48 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-22 08:59:50 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-22 09:14:52 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-22 18:29:55 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-22 19:15:04 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-22 20:15:06 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-22 21:15:04 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-22 22:15:02 | Compressor run ignoring free cooling Opportunity of 2.83 kWh
WLLS1 | RTU32 | 2024-01-22 23:15:01 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-30 05:15:04 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-01-30 06:15:02 | Compressor run ignoring free cooling Opportunity of 2.58 kWh
WLLS1 | RTU32 | 2024-01-30 07:14:59 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-30 08:14:59 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-31 19:45:00 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-01-31 20:44:57 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-31 21:44:57 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-01-31 22:30:07 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-01-31 22:44:54 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-02-01 07:44:58 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-02-07 05:15:06 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-02-07 05:29:55 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-02-07 06:15:07 | Compressor run ignoring free cooling Opportunity of 2.85 kWh
WLLS1 | RTU32 | 2024-02-07 06:29:55 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-02-07 07:15:06 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-02-07 08:15:03 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-02-08 06:00:01 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-02-08 06:59:58 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-02-08 07:45:06 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU32 | 2024-02-08 07:59:53 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU32 | 2024-02-15 05:30:01 | Compressor run ignoring free cooling Opportunity of 2.61 kWh
WLLS1 | RTU32 | 2024-02-18 05:15:00 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-02-18 06:00:00 | Compressor run ignoring free cooling Opportunity of 2.58 kWh
WLLS1 | RTU32 | 2024-02-18 08:00:06 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU32 | 2024-02-18 08:45:00 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-02-18 21:45:03 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU32 | 2024-02-18 22:30:01 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU32 | 2024-04-29 20:29:45 | Compressor run ignoring free cooling Opportunity of 11.30 kWh
WLLS1 | RTU32 | 2024-04-29 20:44:55 | Compressor run ignoring free cooling Opportunity of 11.30 kWh
WLLS1 | RTU32 | 2024-05-01 20:14:59 | Compressor run ignoring free cooling Opportunity of 11.52 kWh
WLLS1 | RTU32 | 2024-05-04 18:00:00 | Compressor run ignoring free cooling Opportunity of 11.25 kWh
WLLS1 | RTU32 | 2024-05-04 19:15:09 | Compressor run ignoring free cooling Opportunity of 10.99 kWh
WLLS1 | RTU32 | 2024-05-04 20:00:05 | Compressor run ignoring free cooling Opportunity of 11.10 kWh
WLLS1 | RTU32 | 2024-05-06 20:14:51 | Compressor run ignoring free cooling Opportunity of 11.17 kWh
WLLS1 | RTU32 | 2024-05-10 18:45:08 | Compressor run ignoring free cooling Opportunity of 11.30 kWh
WLLS1 | RTU32 | 2024-05-10 19:00:00 | Compressor run ignoring free cooling Opportunity of 11.25 kWh
WLLS1 | RTU32 | 2024-05-10 19:14:53 | Compressor run ignoring free cooling Opportunity of 11.23 kWh
WLLS1 | RTU32 | 2024-05-20 20:29:45 | Compressor run ignoring free cooling Opportunity of 11.21 kWh
WLLS1 | RTU32 | 2024-05-21 20:29:45 | Compressor run ignoring free cooling Opportunity of 11.41 kWh
WLLS1 | RTU32 | 2024-05-21 20:44:48 | Compressor run ignoring free cooling Opportunity of 11.46 kWh
WLLS1 | RTU32 | 2024-05-21 20:59:51 | Compressor run ignoring free cooling Opportunity of 11.32 kWh
WLLS1 | RTU32 | 2024-05-21 21:14:56 | Compressor run ignoring free cooling Opportunity of 11.28 kWh
WLLS1 | RTU32 | 2024-05-22 21:44:48 | Compressor run ignoring free cooling Opportunity of 11.37 kWh
WLLS1 | RTU32 | 2024-05-23 20:14:48 | Compressor run ignoring free cooling Opportunity of 11.14 kWh
WLLS1 | RTU32 | 2024-05-23 20:29:55 | Compressor run ignoring free cooling Opportunity of 11.23 kWh
WLLS1 | RTU32 | 2024-05-23 20:45:01 | Compressor run ignoring free cooling Opportunity of 11.19 kWh
WLLS1 | RTU32 | 2024-05-23 21:00:04 | Compressor run ignoring free cooling Opportunity of 11.23 kWh
WLLS1 | RTU32 | 2024-05-24 17:44:44 | Compressor run ignoring free cooling Opportunity of 11.55 kWh
WLLS1 | RTU32 | 2024-05-25 17:59:43 | Compressor run ignoring free cooling Opportunity of 11.19 kWh
WLLS1 | RTU32 | 2024-05-25 18:14:46 | Compressor run ignoring free cooling Opportunity of 10.67 kWh
WLLS1 | RTU32 | 2024-05-25 18:29:50 | Compressor run ignoring free cooling Opportunity of 10.74 kWh
WLLS1 | RTU32 | 2024-05-25 18:44:55 | Compressor run ignoring free cooling Opportunity of 10.83 kWh
WLLS1 | RTU32 | 2024-05-25 18:59:58 | Compressor run ignoring free cooling Opportunity of 10.85 kWh
WLLS1 | RTU32 | 2024-05-25 19:15:02 | Compressor run ignoring free cooling Opportunity of 10.81 kWh
WLLS1 | RTU32 | 2024-05-28 20:59:46 | Compressor run ignoring free cooling Opportunity of 11.28 kWh
WLLS1 | RTU32 | 2024-05-30 20:14:46 | Compressor run ignoring free cooling Opportunity of 10.74 kWh
WLLS1 | RTU32 | 2024-05-30 20:29:49 | Compressor run ignoring free cooling Opportunity of 10.69 kWh
WLLS1 | RTU32 | 2024-05-30 20:44:52 | Compressor run ignoring free cooling Opportunity of 10.58 kWh
WLLS1 | RTU32 | 2024-05-30 20:59:57 | Compressor run ignoring free cooling Opportunity of 10.65 kWh
WLLS1 | RTU32 | 2024-05-31 23:44:53 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU33 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU33 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU33 | 2024-05-31 22:00:04 | No findings on Compressor being run ignoring free cooling Opportunity
WLLS1 | RTU33 | 2024-05-31 22:00:04 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU34 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU34 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU34 | 2024-03-15 17:45:04 | Compressor run ignoring free cooling Opportunity of 19.47 kWh
WLLS1 | RTU34 | 2024-03-20 17:45:05 | Compressor run ignoring free cooling Opportunity of 18.67 kWh
WLLS1 | RTU34 | 2024-03-21 19:15:02 | Compressor run ignoring free cooling Opportunity of 16.38 kWh
WLLS1 | RTU34 | 2024-03-22 19:00:04 | Compressor run ignoring free cooling Opportunity of 16.95 kWh
WLLS1 | RTU34 | 2024-03-30 19:59:58 | Compressor run ignoring free cooling Opportunity of 19.33 kWh
WLLS1 | RTU34 | 2024-03-30 20:15:01 | Compressor run ignoring free cooling Opportunity of 19.11 kWh
WLLS1 | RTU34 | 2024-03-31 22:45:00 | Compressor run ignoring free cooling Opportunity of 19.55 kWh
WLLS1 | RTU34 | 2024-04-02 23:14:59 | Compressor run ignoring free cooling Opportunity of 19.73 kWh
WLLS1 | RTU34 | 2024-05-10 08:30:04 | Compressor run ignoring free cooling Opportunity of 19.38 kWh
WLLS1 | RTU34 | 2024-05-10 08:45:02 | Compressor run ignoring free cooling Opportunity of 19.42 kWh
WLLS1 | RTU34 | 2024-05-13 20:45:03 | Compressor run ignoring free cooling Opportunity of 18.36 kWh
WLLS1 | RTU34 | 2024-05-13 21:30:00 | Compressor run ignoring free cooling Opportunity of 18.36 kWh
WLLS1 | RTU34 | 2024-05-14 06:00:04 | Compressor run ignoring free cooling Opportunity of 18.14 kWh
WLLS1 | RTU34 | 2024-05-14 06:15:02 | Compressor run ignoring free cooling Opportunity of 18.10 kWh
WLLS1 | RTU34 | 2024-05-14 15:45:03 | Compressor run ignoring free cooling Opportunity of 19.47 kWh
WLLS1 | RTU34 | 2024-05-14 16:00:02 | Compressor run ignoring free cooling Opportunity of 19.24 kWh
WLLS1 | RTU34 | 2024-05-15 09:29:58 | Compressor run ignoring free cooling Opportunity of 18.32 kWh
WLLS1 | RTU34 | 2024-05-23 06:14:58 | Compressor run ignoring free cooling Opportunity of 19.24 kWh
WLLS1 | RTU34 | 2024-05-23 06:30:01 | Compressor run ignoring free cooling Opportunity of 19.24 kWh
WLLS1 | RTU34 | 2024-05-23 23:00:01 | Compressor run ignoring free cooling Opportunity of 19.82 kWh
WLLS1 | RTU34 | 2024-05-24 17:45:00 | Compressor run ignoring free cooling Opportunity of 19.77 kWh
WLLS1 | RTU34 | 2024-05-25 05:15:00 | Compressor run ignoring free cooling Opportunity of 19.47 kWh
WLLS1 | RTU34 | 2024-05-25 17:59:59 | Compressor run ignoring free cooling Opportunity of 18.89 kWh
WLLS1 | RTU34 | 2024-05-25 21:15:00 | Compressor run ignoring free cooling Opportunity of 19.42 kWh
WLLS1 | RTU34 | 2024-05-27 06:15:00 | Compressor run ignoring free cooling Opportunity of 19.47 kWh
WLLS1 | RTU34 | 2024-05-27 09:44:58 | Compressor run ignoring free cooling Opportunity of 19.55 kWh
WLLS1 | RTU34 | 2024-05-28 05:44:58 | Compressor run ignoring free cooling Opportunity of 19.42 kWh
WLLS1 | RTU34 | 2024-05-29 21:15:00 | Compressor run ignoring free cooling Opportunity of 20.26 kWh
WLLS1 | RTU34 | 2024-05-30 05:59:58 | Compressor run ignoring free cooling Opportunity of 16.91 kWh
WLLS1 | RTU34 | 2024-05-30 06:15:00 | Compressor run ignoring free cooling Opportunity of 16.95 kWh
WLLS1 | RTU34 | 2024-05-31 08:44:58 | Compressor run ignoring free cooling Opportunity of 19.38 kWh
WLLS1 | RTU34 | 2024-05-31 17:45:02 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU35 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU35 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU35 | 2024-04-29 21:14:50 | Compressor run ignoring free cooling Opportunity of 9.30 kWh
WLLS1 | RTU35 | 2024-04-29 22:29:50 | Compressor run ignoring free cooling Opportunity of 9.26 kWh
WLLS1 | RTU35 | 2024-04-30 21:29:51 | Compressor run ignoring free cooling Opportunity of 9.39 kWh
WLLS1 | RTU35 | 2024-04-30 22:44:50 | Compressor run ignoring free cooling Opportunity of 9.41 kWh
WLLS1 | RTU35 | 2024-05-01 21:15:05 | Compressor run ignoring free cooling Opportunity of 9.50 kWh
WLLS1 | RTU35 | 2024-05-01 22:00:02 | Compressor run ignoring free cooling Opportunity of 9.32 kWh
WLLS1 | RTU35 | 2024-05-02 22:00:02 | Compressor run ignoring free cooling Opportunity of 9.46 kWh
WLLS1 | RTU35 | 2024-05-18 21:14:46 | Compressor run ignoring free cooling Opportunity of 8.90 kWh
WLLS1 | RTU35 | 2024-05-18 21:29:56 | Compressor run ignoring free cooling Opportunity of 8.97 kWh
WLLS1 | RTU35 | 2024-05-22 22:59:46 | Compressor run ignoring free cooling Opportunity of 9.57 kWh
WLLS1 | RTU35 | 2024-05-22 23:14:50 | Compressor run ignoring free cooling Opportunity of 9.52 kWh
WLLS1 | RTU35 | 2024-05-23 21:29:49 | Compressor run ignoring free cooling Opportunity of 9.50 kWh
WLLS1 | RTU35 | 2024-05-23 21:44:52 | Compressor run ignoring free cooling Opportunity of 9.46 kWh
WLLS1 | RTU35 | 2024-05-23 21:59:55 | Compressor run ignoring free cooling Opportunity of 9.48 kWh
WLLS1 | RTU35 | 2024-05-23 22:14:59 | Compressor run ignoring free cooling Opportunity of 9.50 kWh
WLLS1 | RTU35 | 2024-05-23 22:30:02 | Compressor run ignoring free cooling Opportunity of 9.50 kWh
WLLS1 | RTU35 | 2024-05-28 22:29:45 | Compressor run ignoring free cooling Opportunity of 9.32 kWh
WLLS1 | RTU35 | 2024-05-31 23:14:47 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU36 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU36 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU36 | 2024-05-16 20:44:52 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU36 | 2024-05-17 19:44:53 | Compressor run ignoring free cooling Opportunity of 9.16 kWh
WLLS1 | RTU36 | 2024-05-17 20:59:51 | Compressor run ignoring free cooling Opportunity of 9.16 kWh
WLLS1 | RTU36 | 2024-05-22 22:59:52 | Compressor run ignoring free cooling Opportunity of 9.13 kWh
WLLS1 | RTU36 | 2024-05-22 23:14:56 | Compressor run ignoring free cooling Opportunity of 9.07 kWh
WLLS1 | RTU36 | 2024-05-23 21:29:55 | Compressor run ignoring free cooling Opportunity of 9.13 kWh
WLLS1 | RTU36 | 2024-05-23 21:44:58 | Compressor run ignoring free cooling Opportunity of 9.13 kWh
WLLS1 | RTU36 | 2024-05-24 20:00:00 | Compressor run ignoring free cooling Opportunity of 9.18 kWh
WLLS1 | RTU36 | 2024-05-24 22:14:53 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU36 | 2024-05-24 22:29:57 | Compressor run ignoring free cooling Opportunity of 9.16 kWh
WLLS1 | RTU36 | 2024-05-24 22:44:59 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU36 | 2024-05-25 19:44:53 | Compressor run ignoring free cooling Opportunity of 8.95 kWh
WLLS1 | RTU36 | 2024-05-25 19:59:59 | Compressor run ignoring free cooling Opportunity of 8.98 kWh
WLLS1 | RTU36 | 2024-05-31 23:14:53 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU38 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU38 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU38 | 2024-05-31 23:14:57 | No findings on Compressor being run ignoring free cooling Opportunity
WLLS1 | RTU38 | 2024-05-31 23:14:57 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU39 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU39 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU39 | 2024-04-16 20:29:42 | Compressor run ignoring free cooling Opportunity of 14.54 kWh
WLLS1 | RTU39 | 2024-04-18 20:29:44 | Compressor run ignoring free cooling Opportunity of 14.77 kWh
WLLS1 | RTU39 | 2024-04-29 20:29:45 | Compressor run ignoring free cooling Opportunity of 14.45 kWh
WLLS1 | RTU39 | 2024-04-29 20:44:54 | Compressor run ignoring free cooling Opportunity of 14.54 kWh
WLLS1 | RTU39 | 2024-04-30 20:44:43 | Compressor run ignoring free cooling Opportunity of 14.32 kWh
WLLS1 | RTU39 | 2024-04-30 20:59:52 | Compressor run ignoring free cooling Opportunity of 14.59 kWh
WLLS1 | RTU39 | 2024-05-01 20:14:59 | Compressor run ignoring free cooling Opportunity of 14.72 kWh
WLLS1 | RTU39 | 2024-05-04 05:14:59 | Compressor run ignoring free cooling Opportunity of 14.28 kWh
WLLS1 | RTU39 | 2024-05-04 18:00:00 | Compressor run ignoring free cooling Opportunity of 14.28 kWh
WLLS1 | RTU39 | 2024-05-04 19:15:08 | Compressor run ignoring free cooling Opportunity of 14.14 kWh
WLLS1 | RTU39 | 2024-05-08 22:59:42 | Compressor run ignoring free cooling Opportunity of 14.14 kWh
WLLS1 | RTU39 | 2024-05-08 23:14:51 | Compressor run ignoring free cooling Opportunity of 14.14 kWh
WLLS1 | RTU39 | 2024-05-10 18:45:07 | Compressor run ignoring free cooling Opportunity of 14.23 kWh
WLLS1 | RTU39 | 2024-05-10 19:00:00 | Compressor run ignoring free cooling Opportunity of 14.28 kWh
WLLS1 | RTU39 | 2024-05-10 19:14:53 | Compressor run ignoring free cooling Opportunity of 14.28 kWh
WLLS1 | RTU39 | 2024-05-13 18:59:54 | Compressor run ignoring free cooling Opportunity of 14.28 kWh
WLLS1 | RTU39 | 2024-05-13 19:14:53 | Compressor run ignoring free cooling Opportunity of 14.28 kWh
WLLS1 | RTU39 | 2024-05-13 19:29:51 | Compressor run ignoring free cooling Opportunity of 14.23 kWh
WLLS1 | RTU39 | 2024-05-13 19:44:50 | Compressor run ignoring free cooling Opportunity of 14.37 kWh
WLLS1 | RTU39 | 2024-05-13 19:59:47 | Compressor run ignoring free cooling Opportunity of 14.37 kWh
WLLS1 | RTU39 | 2024-05-13 20:14:48 | Compressor run ignoring free cooling Opportunity of 14.37 kWh
WLLS1 | RTU39 | 2024-05-21 20:29:45 | Compressor run ignoring free cooling Opportunity of 14.41 kWh
WLLS1 | RTU39 | 2024-05-21 20:44:48 | Compressor run ignoring free cooling Opportunity of 14.50 kWh
WLLS1 | RTU39 | 2024-05-22 21:44:47 | Compressor run ignoring free cooling Opportunity of 14.45 kWh
WLLS1 | RTU39 | 2024-05-22 21:59:51 | Compressor run ignoring free cooling Opportunity of 14.37 kWh
WLLS1 | RTU39 | 2024-05-23 20:14:47 | Compressor run ignoring free cooling Opportunity of 14.19 kWh
WLLS1 | RTU39 | 2024-05-23 20:29:55 | Compressor run ignoring free cooling Opportunity of 14.37 kWh
WLLS1 | RTU39 | 2024-05-23 20:45:00 | Compressor run ignoring free cooling Opportunity of 14.32 kWh
WLLS1 | RTU39 | 2024-05-23 21:00:04 | Compressor run ignoring free cooling Opportunity of 14.41 kWh
WLLS1 | RTU39 | 2024-05-30 20:14:46 | Compressor run ignoring free cooling Opportunity of 14.05 kWh
WLLS1 | RTU39 | 2024-05-30 20:29:48 | Compressor run ignoring free cooling Opportunity of 14.05 kWh
WLLS1 | RTU39 | 2024-05-30 20:44:52 | Compressor run ignoring free cooling Opportunity of 13.87 kWh
WLLS1 | RTU39 | 2024-05-31 23:44:53 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU4 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU4 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU4 | 2024-04-27 14:59:40 | No findings on Compressor being run ignoring free cooling Opportunity
WLLS1 | RTU4 | 2024-04-27 14:59:40 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU40 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU40 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU40 | 2024-01-03 15:29:42 | Compressor run ignoring free cooling Opportunity of 2.55 kWh
WLLS1 | RTU40 | 2024-01-16 14:14:54 | Compressor run ignoring free cooling Opportunity of 2.45 kWh
WLLS1 | RTU40 | 2024-01-17 10:44:51 | Compressor run ignoring free cooling Opportunity of 2.38 kWh
WLLS1 | RTU40 | 2024-01-24 16:29:55 | Compressor run ignoring free cooling Opportunity of 2.80 kWh
WLLS1 | RTU40 | 2024-01-25 10:14:53 | Compressor run ignoring free cooling Opportunity of 2.70 kWh
WLLS1 | RTU40 | 2024-01-25 12:14:57 | Compressor run ignoring free cooling Opportunity of 2.74 kWh
WLLS1 | RTU40 | 2024-01-26 17:14:55 | Compressor run ignoring free cooling Opportunity of 2.80 kWh
WLLS1 | RTU40 | 2024-02-20 15:15:01 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU40 | 2024-02-21 10:29:57 | Compressor run ignoring free cooling Opportunity of 2.60 kWh
WLLS1 | RTU40 | 2024-03-05 11:59:42 | Compressor run ignoring free cooling Opportunity of 2.73 kWh
WLLS1 | RTU40 | 2024-03-05 16:00:01 | Compressor run ignoring free cooling Opportunity of 2.78 kWh
WLLS1 | RTU40 | 2024-03-06 14:45:00 | Compressor run ignoring free cooling Opportunity of 2.62 kWh
WLLS1 | RTU40 | 2024-03-07 08:59:52 | Compressor run ignoring free cooling Opportunity of 2.71 kWh
WLLS1 | RTU40 | 2024-03-17 17:44:56 | Compressor run ignoring free cooling Opportunity of 2.82 kWh
WLLS1 | RTU40 | 2024-03-19 14:29:40 | Compressor run ignoring free cooling Opportunity of 2.67 kWh
WLLS1 | RTU40 | 2024-03-20 13:29:43 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU40 | 2024-03-26 13:59:45 | Compressor run ignoring free cooling Opportunity of 2.75 kWh
WLLS1 | RTU40 | 2024-03-27 17:00:00 | Compressor run ignoring free cooling Opportunity of 2.63 kWh
WLLS1 | RTU40 | 2024-03-28 13:29:58 | Compressor run ignoring free cooling Opportunity of 2.65 kWh
WLLS1 | RTU40 | 2024-03-31 20:44:55 | Compressor run ignoring free cooling Opportunity of 2.87 kWh
WLLS1 | RTU40 | 2024-04-01 08:29:49 | Compressor run ignoring free cooling Opportunity of 2.77 kWh
WLLS1 | RTU40 | 2024-04-01 21:59:42 | Compressor run ignoring free cooling Opportunity of 2.81 kWh
WLLS1 | RTU40 | 2024-04-11 08:29:43 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU40 | 2024-04-16 09:14:40 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU40 | 2024-05-04 05:14:52 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU40 | 2024-05-04 17:59:52 | Compressor run ignoring free cooling Opportunity of 2.78 kWh
WLLS1 | RTU40 | 2024-05-06 08:30:02 | Compressor run ignoring free cooling Opportunity of 2.80 kWh
WLLS1 | RTU40 | 2024-05-06 20:14:43 | Compressor run ignoring free cooling Opportunity of 2.77 kWh
WLLS1 | RTU40 | 2024-05-07 08:29:38 | Compressor run ignoring free cooling Opportunity of 2.78 kWh
WLLS1 | RTU40 | 2024-05-10 05:14:54 | Compressor run ignoring free cooling Opportunity of 2.69 kWh
WLLS1 | RTU40 | 2024-05-13 09:44:52 | Compressor run ignoring free cooling Opportunity of 2.77 kWh
WLLS1 | RTU40 | 2024-05-14 13:59:46 | Compressor run ignoring free cooling Opportunity of 2.72 kWh
WLLS1 | RTU40 | 2024-05-15 05:14:50 | Compressor run ignoring free cooling Opportunity of 2.69 kWh
WLLS1 | RTU40 | 2024-05-15 08:14:35 | Compressor run ignoring free cooling Opportunity of 2.73 kWh
WLLS1 | RTU40 | 2024-05-19 05:14:48 | Compressor run ignoring free cooling Opportunity of 2.64 kWh
WLLS1 | RTU40 | 2024-05-24 08:29:54 | Compressor run ignoring free cooling Opportunity of 2.75 kWh
WLLS1 | RTU40 | 2024-05-25 05:14:37 | Compressor run ignoring free cooling Opportunity of 2.73 kWh
WLLS1 | RTU40 | 2024-05-27 10:14:42 | Compressor run ignoring free cooling Opportunity of 2.79 kWh
WLLS1 | RTU40 | 2024-05-28 20:59:39 | Compressor run ignoring free cooling Opportunity of 2.77 kWh
WLLS1 | RTU40 | 2024-05-31 21:59:47 | Compressor run ignoring free cooling Opportunity of 2.64 kWh
WLLS1 | RTU40 | 2024-05-31 23:44:46 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU41 | 2024-01-22 07:44:55 | Unit Quick ON/Off within 15 min
WLLS1 | RTU41 | 2024-01-17 05:45:05 | Short Cycling Detected
WLLS1 | RTU41 | 2024-01-17 06:15:07 | Short Cycling Detected
WLLS1 | RTU41 | 2024-01-21 09:59:57 | Short Cycling Detected
WLLS1 | RTU41 | 2024-01-22 07:59:57 | Short Cycling Detected
WLLS1 | RTU41 | 2024-05-31 22:00:04 | No findings on Compressor being run ignoring free cooling Opportunity
WLLS1 | RTU41 | 2024-05-31 22:00:04 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU43 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU43 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU43 | 2024-04-19 22:59:56 | Compressor run ignoring free cooling Opportunity of 2.77 kWh
WLLS1 | RTU43 | 2024-04-29 20:29:54 | Compressor run ignoring free cooling Opportunity of 9.68 kWh
WLLS1 | RTU43 | 2024-05-06 21:29:57 | Compressor run ignoring free cooling Opportunity of 2.77 kWh
WLLS1 | RTU43 | 2024-05-20 22:59:56 | Compressor run ignoring free cooling Opportunity of 2.79 kWh
WLLS1 | RTU43 | 2024-05-21 20:29:54 | Compressor run ignoring free cooling Opportunity of 9.68 kWh
WLLS1 | RTU43 | 2024-05-21 20:44:57 | Compressor run ignoring free cooling Opportunity of 9.66 kWh
WLLS1 | RTU43 | 2024-05-21 21:00:00 | Compressor run ignoring free cooling Opportunity of 9.59 kWh
WLLS1 | RTU43 | 2024-05-25 17:59:52 | Compressor run ignoring free cooling Opportunity of 9.44 kWh
WLLS1 | RTU43 | 2024-05-25 18:14:55 | Compressor run ignoring free cooling Opportunity of 9.41 kWh
WLLS1 | RTU43 | 2024-05-31 21:14:55 | Compressor run ignoring free cooling Opportunity of 2.81 kWh
WLLS1 | RTU43 | 2024-05-31 21:29:58 | Compressor run ignoring free cooling Opportunity of 2.81 kWh
WLLS1 | RTU43 | 2024-05-31 21:45:00 | Compressor run ignoring free cooling Opportunity of 2.81 kWh
WLLS1 | RTU43 | 2024-05-31 22:00:03 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU44 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU44 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU44 | 2024-03-14 20:30:05 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-03-15 17:00:01 | Compressor run ignoring free cooling Opportunity of 9.19 kWh
WLLS1 | RTU44 | 2024-03-15 17:14:56 | Compressor run ignoring free cooling Opportunity of 9.31 kWh
WLLS1 | RTU44 | 2024-03-15 17:29:51 | Compressor run ignoring free cooling Opportunity of 9.16 kWh
WLLS1 | RTU44 | 2024-03-15 17:44:47 | Compressor run ignoring free cooling Opportunity of 9.20 kWh
WLLS1 | RTU44 | 2024-03-16 16:44:52 | Compressor run ignoring free cooling Opportunity of 9.06 kWh
WLLS1 | RTU44 | 2024-03-16 16:59:47 | Compressor run ignoring free cooling Opportunity of 8.98 kWh
WLLS1 | RTU44 | 2024-03-16 18:30:05 | Compressor run ignoring free cooling Opportunity of 9.00 kWh
WLLS1 | RTU44 | 2024-03-16 18:45:00 | Compressor run ignoring free cooling Opportunity of 9.06 kWh
WLLS1 | RTU44 | 2024-03-16 18:59:56 | Compressor run ignoring free cooling Opportunity of 8.91 kWh
WLLS1 | RTU44 | 2024-03-16 19:14:52 | Compressor run ignoring free cooling Opportunity of 8.92 kWh
WLLS1 | RTU44 | 2024-03-16 19:29:47 | Compressor run ignoring free cooling Opportunity of 8.84 kWh
WLLS1 | RTU44 | 2024-03-31 20:29:59 | Compressor run ignoring free cooling Opportunity of 8.80 kWh
WLLS1 | RTU44 | 2024-03-31 20:45:02 | Compressor run ignoring free cooling Opportunity of 8.80 kWh
WLLS1 | RTU44 | 2024-03-31 21:00:04 | Compressor run ignoring free cooling Opportunity of 8.79 kWh
WLLS1 | RTU44 | 2024-04-01 21:44:44 | Compressor run ignoring free cooling Opportunity of 8.83 kWh
WLLS1 | RTU44 | 2024-04-01 21:59:49 | Compressor run ignoring free cooling Opportunity of 8.83 kWh
WLLS1 | RTU44 | 2024-04-01 22:14:53 | Compressor run ignoring free cooling Opportunity of 8.94 kWh
WLLS1 | RTU44 | 2024-04-01 22:29:56 | Compressor run ignoring free cooling Opportunity of 8.84 kWh
WLLS1 | RTU44 | 2024-04-01 22:45:00 | Compressor run ignoring free cooling Opportunity of 8.92 kWh
WLLS1 | RTU44 | 2024-04-02 23:14:42 | Compressor run ignoring free cooling Opportunity of 9.03 kWh
WLLS1 | RTU44 | 2024-04-03 05:14:58 | Compressor run ignoring free cooling Opportunity of 8.97 kWh
WLLS1 | RTU44 | 2024-04-03 05:30:01 | Compressor run ignoring free cooling Opportunity of 8.88 kWh
WLLS1 | RTU44 | 2024-04-03 05:45:03 | Compressor run ignoring free cooling Opportunity of 8.80 kWh
WLLS1 | RTU44 | 2024-04-03 11:29:43 | Compressor run ignoring free cooling Opportunity of 9.06 kWh
WLLS1 | RTU44 | 2024-04-03 13:14:40 | Compressor run ignoring free cooling Opportunity of 9.30 kWh
WLLS1 | RTU44 | 2024-04-03 14:29:42 | Compressor run ignoring free cooling Opportunity of 9.31 kWh
WLLS1 | RTU44 | 2024-04-03 19:14:41 | Compressor run ignoring free cooling Opportunity of 9.06 kWh
WLLS1 | RTU44 | 2024-04-03 20:59:40 | Compressor run ignoring free cooling Opportunity of 8.94 kWh
WLLS1 | RTU44 | 2024-04-08 18:44:50 | Compressor run ignoring free cooling Opportunity of 8.98 kWh
WLLS1 | RTU44 | 2024-04-08 19:29:48 | Compressor run ignoring free cooling Opportunity of 8.86 kWh
WLLS1 | RTU44 | 2024-04-10 21:14:49 | Compressor run ignoring free cooling Opportunity of 9.01 kWh
WLLS1 | RTU44 | 2024-04-10 21:59:47 | Compressor run ignoring free cooling Opportunity of 9.06 kWh
WLLS1 | RTU44 | 2024-04-11 18:14:46 | Compressor run ignoring free cooling Opportunity of 9.11 kWh
WLLS1 | RTU44 | 2024-04-11 18:59:47 | Compressor run ignoring free cooling Opportunity of 8.99 kWh
WLLS1 | RTU44 | 2024-04-12 10:44:48 | Compressor run ignoring free cooling Opportunity of 9.13 kWh
WLLS1 | RTU44 | 2024-04-12 15:14:42 | Compressor run ignoring free cooling Opportunity of 9.08 kWh
WLLS1 | RTU44 | 2024-04-12 17:29:44 | Compressor run ignoring free cooling Opportunity of 9.08 kWh
WLLS1 | RTU44 | 2024-04-15 22:44:43 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-04-16 20:29:41 | Compressor run ignoring free cooling Opportunity of 8.83 kWh
WLLS1 | RTU44 | 2024-04-16 22:44:41 | Compressor run ignoring free cooling Opportunity of 8.82 kWh
WLLS1 | RTU44 | 2024-04-18 20:29:44 | Compressor run ignoring free cooling Opportunity of 8.97 kWh
WLLS1 | RTU44 | 2024-04-18 22:44:44 | Compressor run ignoring free cooling Opportunity of 8.67 kWh
WLLS1 | RTU44 | 2024-04-18 23:00:06 | Compressor run ignoring free cooling Opportunity of 8.70 kWh
WLLS1 | RTU44 | 2024-04-18 23:14:41 | Compressor run ignoring free cooling Opportunity of 8.80 kWh
WLLS1 | RTU44 | 2024-04-19 20:29:50 | Compressor run ignoring free cooling Opportunity of 8.89 kWh
WLLS1 | RTU44 | 2024-04-19 21:44:47 | Compressor run ignoring free cooling Opportunity of 8.88 kWh
WLLS1 | RTU44 | 2024-04-19 21:59:56 | Compressor run ignoring free cooling Opportunity of 8.88 kWh
WLLS1 | RTU44 | 2024-04-19 22:59:46 | Compressor run ignoring free cooling Opportunity of 8.85 kWh
WLLS1 | RTU44 | 2024-04-19 23:14:54 | Compressor run ignoring free cooling Opportunity of 8.86 kWh
WLLS1 | RTU44 | 2024-04-20 19:44:42 | Compressor run ignoring free cooling Opportunity of 9.18 kWh
WLLS1 | RTU44 | 2024-04-20 19:59:51 | Compressor run ignoring free cooling Opportunity of 9.18 kWh
WLLS1 | RTU44 | 2024-04-20 20:59:42 | Compressor run ignoring free cooling Opportunity of 9.04 kWh
WLLS1 | RTU44 | 2024-04-20 21:14:52 | Compressor run ignoring free cooling Opportunity of 9.08 kWh
WLLS1 | RTU44 | 2024-04-20 22:14:42 | Compressor run ignoring free cooling Opportunity of 8.98 kWh
WLLS1 | RTU44 | 2024-04-20 22:29:51 | Compressor run ignoring free cooling Opportunity of 8.94 kWh
WLLS1 | RTU44 | 2024-04-23 18:44:49 | Compressor run ignoring free cooling Opportunity of 9.13 kWh
WLLS1 | RTU44 | 2024-04-24 14:14:50 | Compressor run ignoring free cooling Opportunity of 9.08 kWh
WLLS1 | RTU44 | 2024-04-24 15:29:48 | Compressor run ignoring free cooling Opportunity of 8.80 kWh
WLLS1 | RTU44 | 2024-04-24 15:44:57 | Compressor run ignoring free cooling Opportunity of 8.83 kWh
WLLS1 | RTU44 | 2024-04-25 18:29:53 | Compressor run ignoring free cooling Opportunity of 8.95 kWh
WLLS1 | RTU44 | 2024-04-25 19:29:46 | Compressor run ignoring free cooling Opportunity of 8.91 kWh
WLLS1 | RTU44 | 2024-04-25 19:44:54 | Compressor run ignoring free cooling Opportunity of 8.94 kWh
WLLS1 | RTU44 | 2024-04-25 20:44:43 | Compressor run ignoring free cooling Opportunity of 8.69 kWh
WLLS1 | RTU44 | 2024-04-25 20:59:52 | Compressor run ignoring free cooling Opportunity of 8.61 kWh
WLLS1 | RTU44 | 2024-04-26 16:29:46 | Compressor run ignoring free cooling Opportunity of 9.14 kWh
WLLS1 | RTU44 | 2024-04-26 18:44:42 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-04-26 18:59:52 | Compressor run ignoring free cooling Opportunity of 9.11 kWh
WLLS1 | RTU44 | 2024-04-26 19:59:42 | Compressor run ignoring free cooling Opportunity of 9.00 kWh
WLLS1 | RTU44 | 2024-04-26 20:14:51 | Compressor run ignoring free cooling Opportunity of 8.95 kWh
WLLS1 | RTU44 | 2024-04-26 21:29:50 | Compressor run ignoring free cooling Opportunity of 8.99 kWh
WLLS1 | RTU44 | 2024-04-27 19:14:43 | Compressor run ignoring free cooling Opportunity of 9.19 kWh
WLLS1 | RTU44 | 2024-04-27 19:29:52 | Compressor run ignoring free cooling Opportunity of 9.14 kWh
WLLS1 | RTU44 | 2024-04-27 20:29:43 | Compressor run ignoring free cooling Opportunity of 9.11 kWh
WLLS1 | RTU44 | 2024-04-27 20:44:53 | Compressor run ignoring free cooling Opportunity of 9.13 kWh
WLLS1 | RTU44 | 2024-04-28 20:14:52 | Compressor run ignoring free cooling Opportunity of 9.00 kWh
WLLS1 | RTU44 | 2024-04-28 21:14:44 | Compressor run ignoring free cooling Opportunity of 8.88 kWh
WLLS1 | RTU44 | 2024-04-28 21:29:54 | Compressor run ignoring free cooling Opportunity of 8.93 kWh
WLLS1 | RTU44 | 2024-04-28 22:29:47 | Compressor run ignoring free cooling Opportunity of 8.83 kWh
WLLS1 | RTU44 | 2024-04-29 20:29:44 | Compressor run ignoring free cooling Opportunity of 9.04 kWh
WLLS1 | RTU44 | 2024-04-29 20:44:54 | Compressor run ignoring free cooling Opportunity of 9.16 kWh
WLLS1 | RTU44 | 2024-04-29 21:44:43 | Compressor run ignoring free cooling Opportunity of 9.11 kWh
WLLS1 | RTU44 | 2024-04-29 21:59:52 | Compressor run ignoring free cooling Opportunity of 9.19 kWh
WLLS1 | RTU44 | 2024-04-29 22:59:43 | Compressor run ignoring free cooling Opportunity of 9.03 kWh
WLLS1 | RTU44 | 2024-04-29 23:14:52 | Compressor run ignoring free cooling Opportunity of 8.94 kWh
WLLS1 | RTU44 | 2024-04-30 20:44:42 | Compressor run ignoring free cooling Opportunity of 9.06 kWh
WLLS1 | RTU44 | 2024-04-30 20:59:52 | Compressor run ignoring free cooling Opportunity of 8.95 kWh
WLLS1 | RTU44 | 2024-04-30 21:59:46 | Compressor run ignoring free cooling Opportunity of 8.97 kWh
WLLS1 | RTU44 | 2024-04-30 22:14:55 | Compressor run ignoring free cooling Opportunity of 9.01 kWh
WLLS1 | RTU44 | 2024-04-30 23:14:43 | Compressor run ignoring free cooling Opportunity of 9.00 kWh
WLLS1 | RTU44 | 2024-05-01 05:14:52 | Compressor run ignoring free cooling Opportunity of 8.91 kWh
WLLS1 | RTU44 | 2024-05-01 06:14:41 | Compressor run ignoring free cooling Opportunity of 8.95 kWh
WLLS1 | RTU44 | 2024-05-01 06:29:52 | Compressor run ignoring free cooling Opportunity of 8.95 kWh
WLLS1 | RTU44 | 2024-05-01 20:14:58 | Compressor run ignoring free cooling Opportunity of 8.98 kWh
WLLS1 | RTU44 | 2024-05-01 23:00:07 | Compressor run ignoring free cooling Opportunity of 8.88 kWh
WLLS1 | RTU44 | 2024-05-02 23:00:08 | Compressor run ignoring free cooling Opportunity of 9.14 kWh
WLLS1 | RTU44 | 2024-05-04 05:14:59 | Compressor run ignoring free cooling Opportunity of 11.32 kWh
WLLS1 | RTU44 | 2024-05-04 07:15:04 | Compressor run ignoring free cooling Opportunity of 8.97 kWh
WLLS1 | RTU44 | 2024-05-04 08:00:00 | Compressor run ignoring free cooling Opportunity of 8.89 kWh
WLLS1 | RTU44 | 2024-05-04 17:59:59 | Compressor run ignoring free cooling Opportunity of 9.04 kWh
WLLS1 | RTU44 | 2024-05-04 19:15:07 | Compressor run ignoring free cooling Opportunity of 8.85 kWh
WLLS1 | RTU44 | 2024-05-04 20:00:04 | Compressor run ignoring free cooling Opportunity of 8.73 kWh
WLLS1 | RTU44 | 2024-05-04 20:45:02 | Compressor run ignoring free cooling Opportunity of 8.76 kWh
WLLS1 | RTU44 | 2024-05-04 21:30:00 | Compressor run ignoring free cooling Opportunity of 8.75 kWh
WLLS1 | RTU44 | 2024-05-05 13:15:04 | Compressor run ignoring free cooling Opportunity of 8.84 kWh
WLLS1 | RTU44 | 2024-05-05 14:00:01 | Compressor run ignoring free cooling Opportunity of 8.85 kWh
WLLS1 | RTU44 | 2024-05-05 16:00:04 | Compressor run ignoring free cooling Opportunity of 9.03 kWh
WLLS1 | RTU44 | 2024-05-05 16:45:00 | Compressor run ignoring free cooling Opportunity of 9.04 kWh
WLLS1 | RTU44 | 2024-05-05 20:15:06 | Compressor run ignoring free cooling Opportunity of 9.08 kWh
WLLS1 | RTU44 | 2024-05-05 21:00:03 | Compressor run ignoring free cooling Opportunity of 8.99 kWh
WLLS1 | RTU44 | 2024-05-05 21:45:02 | Compressor run ignoring free cooling Opportunity of 8.95 kWh
WLLS1 | RTU44 | 2024-05-06 05:45:00 | Compressor run ignoring free cooling Opportunity of 9.27 kWh
WLLS1 | RTU44 | 2024-05-06 06:29:58 | Compressor run ignoring free cooling Opportunity of 9.18 kWh
WLLS1 | RTU44 | 2024-05-06 07:14:56 | Compressor run ignoring free cooling Opportunity of 9.25 kWh
WLLS1 | RTU44 | 2024-05-06 09:15:05 | Compressor run ignoring free cooling Opportunity of 9.39 kWh
WLLS1 | RTU44 | 2024-05-06 20:14:50 | Compressor run ignoring free cooling Opportunity of 8.91 kWh
WLLS1 | RTU44 | 2024-05-06 21:29:47 | Compressor run ignoring free cooling Opportunity of 8.82 kWh
WLLS1 | RTU44 | 2024-05-06 21:44:57 | Compressor run ignoring free cooling Opportunity of 8.81 kWh
WLLS1 | RTU44 | 2024-05-06 22:44:50 | Compressor run ignoring free cooling Opportunity of 8.90 kWh
WLLS1 | RTU44 | 2024-05-07 05:59:44 | Compressor run ignoring free cooling Opportunity of 9.00 kWh
WLLS1 | RTU44 | 2024-05-07 06:14:55 | Compressor run ignoring free cooling Opportunity of 9.01 kWh
WLLS1 | RTU44 | 2024-05-07 07:14:45 | Compressor run ignoring free cooling Opportunity of 9.04 kWh
WLLS1 | RTU44 | 2024-05-07 07:29:55 | Compressor run ignoring free cooling Opportunity of 9.11 kWh
WLLS1 | RTU44 | 2024-05-07 08:29:45 | Compressor run ignoring free cooling Opportunity of 9.07 kWh
WLLS1 | RTU44 | 2024-05-07 08:44:55 | Compressor run ignoring free cooling Opportunity of 9.10 kWh
WLLS1 | RTU44 | 2024-05-08 06:15:07 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-05-08 07:00:02 | Compressor run ignoring free cooling Opportunity of 9.23 kWh
WLLS1 | RTU44 | 2024-05-08 22:59:41 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-05-08 23:14:50 | Compressor run ignoring free cooling Opportunity of 9.12 kWh
WLLS1 | RTU44 | 2024-05-09 05:59:46 | Compressor run ignoring free cooling Opportunity of 9.21 kWh
WLLS1 | RTU44 | 2024-05-09 06:14:55 | Compressor run ignoring free cooling Opportunity of 9.22 kWh
WLLS1 | RTU44 | 2024-05-09 07:14:41 | Compressor run ignoring free cooling Opportunity of 9.10 kWh
WLLS1 | RTU44 | 2024-05-09 07:29:50 | Compressor run ignoring free cooling Opportunity of 9.11 kWh
WLLS1 | RTU44 | 2024-05-09 07:44:59 | Compressor run ignoring free cooling Opportunity of 9.02 kWh
WLLS1 | RTU44 | 2024-05-09 08:29:42 | Compressor run ignoring free cooling Opportunity of 9.14 kWh
WLLS1 | RTU44 | 2024-05-09 09:14:42 | Compressor run ignoring free cooling Opportunity of 9.17 kWh
WLLS1 | RTU44 | 2024-05-09 20:30:00 | Compressor run ignoring free cooling Opportunity of 9.20 kWh
WLLS1 | RTU44 | 2024-05-09 20:44:58 | Compressor run ignoring free cooling Opportunity of 9.20 kWh
WLLS1 | RTU44 | 2024-05-09 20:59:57 | Compressor run ignoring free cooling Opportunity of 9.13 kWh
WLLS1 | RTU44 | 2024-05-09 21:14:54 | Compressor run ignoring free cooling Opportunity of 9.14 kWh
WLLS1 | RTU44 | 2024-05-09 21:29:54 | Compressor run ignoring free cooling Opportunity of 9.19 kWh
WLLS1 | RTU44 | 2024-05-09 21:44:54 | Compressor run ignoring free cooling Opportunity of 9.27 kWh
WLLS1 | RTU44 | 2024-05-09 21:59:52 | Compressor run ignoring free cooling Opportunity of 9.16 kWh
WLLS1 | RTU44 | 2024-05-09 22:14:52 | Compressor run ignoring free cooling Opportunity of 9.20 kWh
WLLS1 | RTU44 | 2024-05-09 22:29:52 | Compressor run ignoring free cooling Opportunity of 9.25 kWh
WLLS1 | RTU44 | 2024-05-09 22:44:50 | Compressor run ignoring free cooling Opportunity of 9.27 kWh
WLLS1 | RTU44 | 2024-05-09 22:59:48 | Compressor run ignoring free cooling Opportunity of 9.19 kWh
WLLS1 | RTU44 | 2024-05-09 23:14:48 | Compressor run ignoring free cooling Opportunity of 9.21 kWh
WLLS1 | RTU44 | 2024-05-10 07:29:53 | Compressor run ignoring free cooling Opportunity of 9.01 kWh
WLLS1 | RTU44 | 2024-05-10 07:44:51 | Compressor run ignoring free cooling Opportunity of 9.00 kWh
WLLS1 | RTU44 | 2024-05-10 07:59:49 | Compressor run ignoring free cooling Opportunity of 9.01 kWh
WLLS1 | RTU44 | 2024-05-10 08:14:47 | Compressor run ignoring free cooling Opportunity of 9.16 kWh
WLLS1 | RTU44 | 2024-05-10 08:29:45 | Compressor run ignoring free cooling Opportunity of 9.26 kWh
WLLS1 | RTU44 | 2024-05-10 08:44:43 | Compressor run ignoring free cooling Opportunity of 9.17 kWh
WLLS1 | RTU44 | 2024-05-10 18:45:06 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-05-10 18:59:59 | Compressor run ignoring free cooling Opportunity of 9.13 kWh
WLLS1 | RTU44 | 2024-05-10 19:14:52 | Compressor run ignoring free cooling Opportunity of 9.14 kWh
WLLS1 | RTU44 | 2024-05-10 20:30:04 | Compressor run ignoring free cooling Opportunity of 8.88 kWh
WLLS1 | RTU44 | 2024-05-10 20:44:56 | Compressor run ignoring free cooling Opportunity of 8.89 kWh
WLLS1 | RTU44 | 2024-05-10 20:59:48 | Compressor run ignoring free cooling Opportunity of 8.72 kWh
WLLS1 | RTU44 | 2024-05-10 22:15:02 | Compressor run ignoring free cooling Opportunity of 8.75 kWh
WLLS1 | RTU44 | 2024-05-10 22:29:55 | Compressor run ignoring free cooling Opportunity of 8.88 kWh
WLLS1 | RTU44 | 2024-05-11 12:14:51 | Compressor run ignoring free cooling Opportunity of 9.17 kWh
WLLS1 | RTU44 | 2024-05-11 13:44:56 | Compressor run ignoring free cooling Opportunity of 8.99 kWh
WLLS1 | RTU44 | 2024-05-11 15:15:02 | Compressor run ignoring free cooling Opportunity of 9.01 kWh
WLLS1 | RTU44 | 2024-05-11 18:59:50 | Compressor run ignoring free cooling Opportunity of 9.10 kWh
WLLS1 | RTU44 | 2024-05-11 20:15:05 | Compressor run ignoring free cooling Opportunity of 8.84 kWh
WLLS1 | RTU44 | 2024-05-11 20:30:00 | Compressor run ignoring free cooling Opportunity of 8.86 kWh
WLLS1 | RTU44 | 2024-05-11 20:44:54 | Compressor run ignoring free cooling Opportunity of 8.84 kWh
WLLS1 | RTU44 | 2024-05-11 22:00:05 | Compressor run ignoring free cooling Opportunity of 8.91 kWh
WLLS1 | RTU44 | 2024-05-11 22:14:58 | Compressor run ignoring free cooling Opportunity of 8.89 kWh
WLLS1 | RTU44 | 2024-05-11 22:29:51 | Compressor run ignoring free cooling Opportunity of 8.92 kWh
WLLS1 | RTU44 | 2024-05-12 20:30:06 | Compressor run ignoring free cooling Opportunity of 8.67 kWh
WLLS1 | RTU44 | 2024-05-12 20:44:58 | Compressor run ignoring free cooling Opportunity of 8.62 kWh
WLLS1 | RTU44 | 2024-05-12 20:59:52 | Compressor run ignoring free cooling Opportunity of 8.72 kWh
WLLS1 | RTU44 | 2024-05-12 22:15:04 | Compressor run ignoring free cooling Opportunity of 8.62 kWh
WLLS1 | RTU44 | 2024-05-12 22:29:58 | Compressor run ignoring free cooling Opportunity of 8.63 kWh
WLLS1 | RTU44 | 2024-05-12 22:44:50 | Compressor run ignoring free cooling Opportunity of 8.78 kWh
WLLS1 | RTU44 | 2024-05-13 18:59:54 | Compressor run ignoring free cooling Opportunity of 9.35 kWh
WLLS1 | RTU44 | 2024-05-13 19:14:53 | Compressor run ignoring free cooling Opportunity of 9.27 kWh
WLLS1 | RTU44 | 2024-05-13 19:29:50 | Compressor run ignoring free cooling Opportunity of 9.30 kWh
WLLS1 | RTU44 | 2024-05-13 19:44:49 | Compressor run ignoring free cooling Opportunity of 9.40 kWh
WLLS1 | RTU44 | 2024-05-13 19:59:47 | Compressor run ignoring free cooling Opportunity of 9.29 kWh
WLLS1 | RTU44 | 2024-05-13 20:14:47 | Compressor run ignoring free cooling Opportunity of 9.21 kWh
WLLS1 | RTU44 | 2024-05-13 20:29:47 | Compressor run ignoring free cooling Opportunity of 9.27 kWh
WLLS1 | RTU44 | 2024-05-13 20:44:45 | Compressor run ignoring free cooling Opportunity of 9.31 kWh
WLLS1 | RTU44 | 2024-05-13 21:29:42 | Compressor run ignoring free cooling Opportunity of 9.02 kWh
WLLS1 | RTU44 | 2024-05-14 14:29:52 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-05-14 14:44:51 | Compressor run ignoring free cooling Opportunity of 9.07 kWh
WLLS1 | RTU44 | 2024-05-14 14:59:50 | Compressor run ignoring free cooling Opportunity of 9.16 kWh
WLLS1 | RTU44 | 2024-05-14 15:14:47 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-05-14 15:29:47 | Compressor run ignoring free cooling Opportunity of 9.08 kWh
WLLS1 | RTU44 | 2024-05-14 15:44:45 | Compressor run ignoring free cooling Opportunity of 9.04 kWh
WLLS1 | RTU44 | 2024-05-14 15:59:43 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-05-15 12:00:05 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-05-15 12:15:05 | Compressor run ignoring free cooling Opportunity of 9.04 kWh
WLLS1 | RTU44 | 2024-05-15 20:30:06 | Compressor run ignoring free cooling Opportunity of 9.00 kWh
WLLS1 | RTU44 | 2024-05-15 20:45:06 | Compressor run ignoring free cooling Opportunity of 8.97 kWh
WLLS1 | RTU44 | 2024-05-15 21:00:06 | Compressor run ignoring free cooling Opportunity of 8.93 kWh
WLLS1 | RTU44 | 2024-05-15 21:15:04 | Compressor run ignoring free cooling Opportunity of 9.06 kWh
WLLS1 | RTU44 | 2024-05-15 21:30:02 | Compressor run ignoring free cooling Opportunity of 9.00 kWh
WLLS1 | RTU44 | 2024-05-15 21:45:01 | Compressor run ignoring free cooling Opportunity of 9.00 kWh
WLLS1 | RTU44 | 2024-05-15 21:59:58 | Compressor run ignoring free cooling Opportunity of 8.97 kWh
WLLS1 | RTU44 | 2024-05-15 22:14:57 | Compressor run ignoring free cooling Opportunity of 8.88 kWh
WLLS1 | RTU44 | 2024-05-15 22:29:55 | Compressor run ignoring free cooling Opportunity of 8.94 kWh
WLLS1 | RTU44 | 2024-05-15 22:44:55 | Compressor run ignoring free cooling Opportunity of 8.95 kWh
WLLS1 | RTU44 | 2024-05-15 22:59:53 | Compressor run ignoring free cooling Opportunity of 8.98 kWh
WLLS1 | RTU44 | 2024-05-15 23:14:52 | Compressor run ignoring free cooling Opportunity of 8.91 kWh
WLLS1 | RTU44 | 2024-05-16 21:14:42 | Compressor run ignoring free cooling Opportunity of 9.02 kWh
WLLS1 | RTU44 | 2024-05-16 21:29:52 | Compressor run ignoring free cooling Opportunity of 8.97 kWh
WLLS1 | RTU44 | 2024-05-16 22:29:44 | Compressor run ignoring free cooling Opportunity of 9.03 kWh
WLLS1 | RTU44 | 2024-05-16 22:44:53 | Compressor run ignoring free cooling Opportunity of 8.98 kWh
WLLS1 | RTU44 | 2024-05-17 05:29:46 | Compressor run ignoring free cooling Opportunity of 9.06 kWh
WLLS1 | RTU44 | 2024-05-17 05:44:55 | Compressor run ignoring free cooling Opportunity of 8.97 kWh
WLLS1 | RTU44 | 2024-05-17 06:44:49 | Compressor run ignoring free cooling Opportunity of 9.10 kWh
WLLS1 | RTU44 | 2024-05-17 07:44:43 | Compressor run ignoring free cooling Opportunity of 9.27 kWh
WLLS1 | RTU44 | 2024-05-17 19:14:50 | Compressor run ignoring free cooling Opportunity of 8.98 kWh
WLLS1 | RTU44 | 2024-05-17 20:14:42 | Compressor run ignoring free cooling Opportunity of 9.02 kWh
WLLS1 | RTU44 | 2024-05-17 20:29:51 | Compressor run ignoring free cooling Opportunity of 9.07 kWh
WLLS1 | RTU44 | 2024-05-17 21:44:45 | Compressor run ignoring free cooling Opportunity of 9.14 kWh
WLLS1 | RTU44 | 2024-05-17 21:59:56 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-05-17 22:59:49 | Compressor run ignoring free cooling Opportunity of 9.06 kWh
WLLS1 | RTU44 | 2024-05-18 05:59:42 | Compressor run ignoring free cooling Opportunity of 9.02 kWh
WLLS1 | RTU44 | 2024-05-18 06:14:52 | Compressor run ignoring free cooling Opportunity of 9.11 kWh
WLLS1 | RTU44 | 2024-05-18 08:44:49 | Compressor run ignoring free cooling Opportunity of 9.20 kWh
WLLS1 | RTU44 | 2024-05-18 18:14:42 | Compressor run ignoring free cooling Opportunity of 11.32 kWh
WLLS1 | RTU44 | 2024-05-18 18:29:53 | Compressor run ignoring free cooling Opportunity of 11.32 kWh
WLLS1 | RTU44 | 2024-05-18 19:29:48 | Compressor run ignoring free cooling Opportunity of 9.01 kWh
WLLS1 | RTU44 | 2024-05-18 20:44:46 | Compressor run ignoring free cooling Opportunity of 8.82 kWh
WLLS1 | RTU44 | 2024-05-18 21:59:52 | Compressor run ignoring free cooling Opportunity of 8.83 kWh
WLLS1 | RTU44 | 2024-05-18 23:14:50 | Compressor run ignoring free cooling Opportunity of 8.91 kWh
WLLS1 | RTU44 | 2024-05-19 18:14:47 | Compressor run ignoring free cooling Opportunity of 9.07 kWh
WLLS1 | RTU44 | 2024-05-19 19:14:41 | Compressor run ignoring free cooling Opportunity of 9.10 kWh
WLLS1 | RTU44 | 2024-05-19 19:29:50 | Compressor run ignoring free cooling Opportunity of 9.07 kWh
WLLS1 | RTU44 | 2024-05-19 20:29:44 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-05-19 20:44:52 | Compressor run ignoring free cooling Opportunity of 9.06 kWh
WLLS1 | RTU44 | 2024-05-19 21:44:45 | Compressor run ignoring free cooling Opportunity of 8.88 kWh
WLLS1 | RTU44 | 2024-05-19 22:59:49 | Compressor run ignoring free cooling Opportunity of 8.78 kWh
WLLS1 | RTU44 | 2024-05-20 20:29:44 | Compressor run ignoring free cooling Opportunity of 8.86 kWh
WLLS1 | RTU44 | 2024-05-20 20:44:53 | Compressor run ignoring free cooling Opportunity of 8.85 kWh
WLLS1 | RTU44 | 2024-05-20 21:44:45 | Compressor run ignoring free cooling Opportunity of 8.84 kWh
WLLS1 | RTU44 | 2024-05-20 21:59:54 | Compressor run ignoring free cooling Opportunity of 8.82 kWh
WLLS1 | RTU44 | 2024-05-20 22:59:46 | Compressor run ignoring free cooling Opportunity of 8.86 kWh
WLLS1 | RTU44 | 2024-05-20 23:14:54 | Compressor run ignoring free cooling Opportunity of 8.85 kWh
WLLS1 | RTU44 | 2024-05-21 20:29:44 | Compressor run ignoring free cooling Opportunity of 9.07 kWh
WLLS1 | RTU44 | 2024-05-21 20:44:47 | Compressor run ignoring free cooling Opportunity of 9.08 kWh
WLLS1 | RTU44 | 2024-05-21 20:59:50 | Compressor run ignoring free cooling Opportunity of 9.08 kWh
WLLS1 | RTU44 | 2024-05-21 21:14:55 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-05-21 21:29:59 | Compressor run ignoring free cooling Opportunity of 9.04 kWh
WLLS1 | RTU44 | 2024-05-21 21:45:02 | Compressor run ignoring free cooling Opportunity of 8.94 kWh
WLLS1 | RTU44 | 2024-05-22 21:44:47 | Compressor run ignoring free cooling Opportunity of 9.02 kWh
WLLS1 | RTU44 | 2024-05-22 21:59:51 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-05-23 06:14:41 | Compressor run ignoring free cooling Opportunity of 9.00 kWh
WLLS1 | RTU44 | 2024-05-23 06:29:44 | Compressor run ignoring free cooling Opportunity of 9.03 kWh
WLLS1 | RTU44 | 2024-05-23 06:44:47 | Compressor run ignoring free cooling Opportunity of 9.02 kWh
WLLS1 | RTU44 | 2024-05-23 06:59:51 | Compressor run ignoring free cooling Opportunity of 8.95 kWh
WLLS1 | RTU44 | 2024-05-23 07:14:55 | Compressor run ignoring free cooling Opportunity of 9.08 kWh
WLLS1 | RTU44 | 2024-05-23 07:29:59 | Compressor run ignoring free cooling Opportunity of 9.14 kWh
WLLS1 | RTU44 | 2024-05-23 20:14:47 | Compressor run ignoring free cooling Opportunity of 11.32 kWh
WLLS1 | RTU44 | 2024-05-23 20:29:54 | Compressor run ignoring free cooling Opportunity of 11.32 kWh
WLLS1 | RTU44 | 2024-05-23 20:45:00 | Compressor run ignoring free cooling Opportunity of 11.32 kWh
WLLS1 | RTU44 | 2024-05-23 21:00:03 | Compressor run ignoring free cooling Opportunity of 8.90 kWh
WLLS1 | RTU44 | 2024-05-23 22:59:44 | Compressor run ignoring free cooling Opportunity of 9.06 kWh
WLLS1 | RTU44 | 2024-05-23 23:14:47 | Compressor run ignoring free cooling Opportunity of 9.08 kWh
WLLS1 | RTU44 | 2024-05-24 05:15:04 | Compressor run ignoring free cooling Opportunity of 11.32 kWh
WLLS1 | RTU44 | 2024-05-24 07:14:44 | Compressor run ignoring free cooling Opportunity of 9.04 kWh
WLLS1 | RTU44 | 2024-05-24 07:29:47 | Compressor run ignoring free cooling Opportunity of 9.12 kWh
WLLS1 | RTU44 | 2024-05-24 07:44:52 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-05-24 07:59:55 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-05-24 08:14:57 | Compressor run ignoring free cooling Opportunity of 9.13 kWh
WLLS1 | RTU44 | 2024-05-24 08:30:00 | Compressor run ignoring free cooling Opportunity of 9.17 kWh
WLLS1 | RTU44 | 2024-05-24 17:44:43 | Compressor run ignoring free cooling Opportunity of 11.32 kWh
WLLS1 | RTU44 | 2024-05-24 20:59:45 | Compressor run ignoring free cooling Opportunity of 9.04 kWh
WLLS1 | RTU44 | 2024-05-24 21:14:50 | Compressor run ignoring free cooling Opportunity of 9.03 kWh
WLLS1 | RTU44 | 2024-05-24 21:29:57 | Compressor run ignoring free cooling Opportunity of 9.01 kWh
WLLS1 | RTU44 | 2024-05-24 21:45:01 | Compressor run ignoring free cooling Opportunity of 9.01 kWh
WLLS1 | RTU44 | 2024-05-25 17:59:42 | Compressor run ignoring free cooling Opportunity of 11.32 kWh
WLLS1 | RTU44 | 2024-05-25 18:14:45 | Compressor run ignoring free cooling Opportunity of 11.32 kWh
WLLS1 | RTU44 | 2024-05-25 18:29:49 | Compressor run ignoring free cooling Opportunity of 11.32 kWh
WLLS1 | RTU44 | 2024-05-25 18:44:53 | Compressor run ignoring free cooling Opportunity of 9.04 kWh
WLLS1 | RTU44 | 2024-05-25 18:59:57 | Compressor run ignoring free cooling Opportunity of 8.94 kWh
WLLS1 | RTU44 | 2024-05-25 19:15:01 | Compressor run ignoring free cooling Opportunity of 9.14 kWh
WLLS1 | RTU44 | 2024-05-25 21:14:43 | Compressor run ignoring free cooling Opportunity of 9.04 kWh
WLLS1 | RTU44 | 2024-05-25 21:29:47 | Compressor run ignoring free cooling Opportunity of 9.11 kWh
WLLS1 | RTU44 | 2024-05-25 21:44:50 | Compressor run ignoring free cooling Opportunity of 9.23 kWh
WLLS1 | RTU44 | 2024-05-25 21:59:53 | Compressor run ignoring free cooling Opportunity of 9.09 kWh
WLLS1 | RTU44 | 2024-05-25 22:14:56 | Compressor run ignoring free cooling Opportunity of 9.08 kWh
WLLS1 | RTU44 | 2024-05-25 22:29:58 | Compressor run ignoring free cooling Opportunity of 9.04 kWh
WLLS1 | RTU44 | 2024-05-25 22:45:02 | Compressor run ignoring free cooling Opportunity of 9.14 kWh
WLLS1 | RTU44 | 2024-05-26 05:29:49 | Compressor run ignoring free cooling Opportunity of 8.93 kWh
WLLS1 | RTU44 | 2024-05-26 05:44:52 | Compressor run ignoring free cooling Opportunity of 8.95 kWh
WLLS1 | RTU44 | 2024-05-26 05:59:57 | Compressor run ignoring free cooling Opportunity of 8.95 kWh
WLLS1 | RTU44 | 2024-05-26 06:15:01 | Compressor run ignoring free cooling Opportunity of 8.92 kWh
WLLS1 | RTU44 | 2024-05-27 06:14:42 | Compressor run ignoring free cooling Opportunity of 9.13 kWh
WLLS1 | RTU44 | 2024-05-27 06:29:44 | Compressor run ignoring free cooling Opportunity of 9.02 kWh
WLLS1 | RTU44 | 2024-05-27 06:44:49 | Compressor run ignoring free cooling Opportunity of 9.08 kWh
WLLS1 | RTU44 | 2024-05-27 06:59:53 | Compressor run ignoring free cooling Opportunity of 9.07 kWh
WLLS1 | RTU44 | 2024-05-27 07:14:57 | Compressor run ignoring free cooling Opportunity of 9.11 kWh
WLLS1 | RTU44 | 2024-05-27 07:30:01 | Compressor run ignoring free cooling Opportunity of 9.06 kWh
WLLS1 | RTU44 | 2024-05-27 09:44:41 | Compressor run ignoring free cooling Opportunity of 9.12 kWh
WLLS1 | RTU44 | 2024-05-27 09:59:44 | Compressor run ignoring free cooling Opportunity of 9.14 kWh
WLLS1 | RTU44 | 2024-05-27 10:14:48 | Compressor run ignoring free cooling Opportunity of 9.10 kWh
WLLS1 | RTU44 | 2024-05-27 10:29:51 | Compressor run ignoring free cooling Opportunity of 9.26 kWh
WLLS1 | RTU44 | 2024-05-28 05:44:41 | Compressor run ignoring free cooling Opportunity of 8.95 kWh
WLLS1 | RTU44 | 2024-05-28 05:59:45 | Compressor run ignoring free cooling Opportunity of 8.93 kWh
WLLS1 | RTU44 | 2024-05-28 06:14:49 | Compressor run ignoring free cooling Opportunity of 8.97 kWh
WLLS1 | RTU44 | 2024-05-28 06:29:53 | Compressor run ignoring free cooling Opportunity of 8.99 kWh
WLLS1 | RTU44 | 2024-05-28 06:44:57 | Compressor run ignoring free cooling Opportunity of 9.02 kWh
WLLS1 | RTU44 | 2024-05-28 07:00:01 | Compressor run ignoring free cooling Opportunity of 9.16 kWh
WLLS1 | RTU44 | 2024-05-28 20:59:45 | Compressor run ignoring free cooling Opportunity of 8.93 kWh
WLLS1 | RTU44 | 2024-05-29 21:14:42 | Compressor run ignoring free cooling Opportunity of 8.79 kWh
WLLS1 | RTU44 | 2024-05-29 21:29:45 | Compressor run ignoring free cooling Opportunity of 8.83 kWh
WLLS1 | RTU44 | 2024-05-29 21:44:48 | Compressor run ignoring free cooling Opportunity of 8.84 kWh
WLLS1 | RTU44 | 2024-05-29 21:59:50 | Compressor run ignoring free cooling Opportunity of 8.86 kWh
WLLS1 | RTU44 | 2024-05-29 22:14:53 | Compressor run ignoring free cooling Opportunity of 8.79 kWh
WLLS1 | RTU44 | 2024-05-29 22:29:56 | Compressor run ignoring free cooling Opportunity of 9.01 kWh
WLLS1 | RTU44 | 2024-05-29 22:44:59 | Compressor run ignoring free cooling Opportunity of 9.01 kWh
WLLS1 | RTU44 | 2024-05-29 23:00:01 | Compressor run ignoring free cooling Opportunity of 9.02 kWh
WLLS1 | RTU44 | 2024-05-30 09:44:43 | Compressor run ignoring free cooling Opportunity of 9.06 kWh
WLLS1 | RTU44 | 2024-05-30 09:59:49 | Compressor run ignoring free cooling Opportunity of 9.10 kWh
WLLS1 | RTU44 | 2024-05-30 10:14:53 | Compressor run ignoring free cooling Opportunity of 9.19 kWh
WLLS1 | RTU44 | 2024-05-30 20:14:45 | Compressor run ignoring free cooling Opportunity of 8.78 kWh
WLLS1 | RTU44 | 2024-05-30 20:29:48 | Compressor run ignoring free cooling Opportunity of 8.81 kWh
WLLS1 | RTU44 | 2024-05-30 20:44:51 | Compressor run ignoring free cooling Opportunity of 8.69 kWh
WLLS1 | RTU44 | 2024-05-30 20:59:55 | Compressor run ignoring free cooling Opportunity of 8.61 kWh
WLLS1 | RTU44 | 2024-05-30 21:14:59 | Compressor run ignoring free cooling Opportunity of 8.64 kWh
WLLS1 | RTU44 | 2024-05-30 21:30:01 | Compressor run ignoring free cooling Opportunity of 8.64 kWh
WLLS1 | RTU44 | 2024-05-31 21:14:45 | Compressor run ignoring free cooling Opportunity of 8.76 kWh
WLLS1 | RTU44 | 2024-05-31 21:29:47 | Compressor run ignoring free cooling Opportunity of 8.73 kWh
WLLS1 | RTU44 | 2024-05-31 21:44:50 | Compressor run ignoring free cooling Opportunity of 8.76 kWh
WLLS1 | RTU44 | 2024-05-31 21:59:53 | Compressor run ignoring free cooling Opportunity of 8.75 kWh
WLLS1 | RTU44 | 2024-05-31 22:14:58 | Compressor run ignoring free cooling Opportunity of 8.71 kWh
WLLS1 | RTU44 | 2024-05-31 22:30:01 | Compressor run ignoring free cooling Opportunity of 8.69 kWh
WLLS1 | RTU44 | 2024-05-31 22:45:04 | Compressor run ignoring free cooling Opportunity of 8.69 kWh
WLLS1 | RTU44 | 2024-05-31 23:44:52 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU45 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU45 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU45 | 2024-05-31 23:44:51 | No findings on Compressor being run ignoring free cooling Opportunity
WLLS1 | RTU45 | 2024-05-31 23:44:51 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU46 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU46 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU46 | 2024-03-12 13:45:05 | Compressor run ignoring free cooling Opportunity of 3.57 kWh
WLLS1 | RTU46 | 2024-03-12 14:00:02 | Compressor run ignoring free cooling Opportunity of 3.58 kWh
WLLS1 | RTU46 | 2024-03-12 19:00:00 | Compressor run ignoring free cooling Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-03-13 19:30:02 | Compressor run ignoring free cooling Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-03-13 19:44:56 | Compressor run ignoring free cooling Opportunity of 1.46 kWh
WLLS1 | RTU46 | 2024-03-14 21:00:04 | Compressor run ignoring free cooling Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-03-15 19:45:06 | Compressor run ignoring free cooling Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-03-15 20:00:02 | Compressor run ignoring free cooling Opportunity of 1.46 kWh
WLLS1 | RTU46 | 2024-03-15 20:14:59 | Compressor run ignoring free cooling Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-03-16 16:45:01 | Compressor run ignoring free cooling Opportunity of 3.57 kWh
WLLS1 | RTU46 | 2024-03-16 16:59:56 | Compressor run ignoring free cooling Opportunity of 3.52 kWh
WLLS1 | RTU46 | 2024-03-16 19:15:00 | Compressor run ignoring free cooling Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-03-16 19:29:56 | Compressor run ignoring free cooling Opportunity of 1.46 kWh
WLLS1 | RTU46 | 2024-03-19 18:00:05 | Compressor run ignoring free cooling Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-03-19 18:15:03 | Compressor run ignoring free cooling Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-03-20 17:15:00 | Compressor run ignoring free cooling Opportunity of 3.50 kWh
WLLS1 | RTU46 | 2024-03-20 17:29:57 | Compressor run ignoring free cooling Opportunity of 3.56 kWh
WLLS1 | RTU46 | 2024-03-20 17:44:56 | Compressor run ignoring free cooling Opportunity of 3.55 kWh
WLLS1 | RTU46 | 2024-03-21 14:30:05 | Compressor run ignoring free cooling Opportunity of 3.47 kWh
WLLS1 | RTU46 | 2024-03-21 14:45:02 | Compressor run ignoring free cooling Opportunity of 3.50 kWh
WLLS1 | RTU46 | 2024-03-21 14:59:57 | Compressor run ignoring free cooling Opportunity of 3.46 kWh
WLLS1 | RTU46 | 2024-03-21 15:14:54 | Compressor run ignoring free cooling Opportunity of 3.54 kWh
WLLS1 | RTU46 | 2024-03-21 18:15:04 | Compressor run ignoring free cooling Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-03-21 18:30:04 | Compressor run ignoring free cooling Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-03-21 18:45:01 | Compressor run ignoring free cooling Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-03-21 18:59:57 | Compressor run ignoring free cooling Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-03-25 18:30:03 | Compressor run ignoring free cooling Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-03-31 22:44:52 | Compressor run ignoring free cooling Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-04-02 23:14:51 | Compressor run ignoring free cooling Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-04-05 16:44:51 | Compressor run ignoring free cooling Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-04-05 16:59:54 | Compressor run ignoring free cooling Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-04-05 17:14:57 | Compressor run ignoring free cooling Opportunity of 1.46 kWh
WLLS1 | RTU46 | 2024-04-05 17:30:01 | Compressor run ignoring free cooling Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-04-06 15:29:52 | Compressor run ignoring free cooling Opportunity of 1.47 kWh
WLLS1 | RTU46 | 2024-04-06 15:44:56 | Compressor run ignoring free cooling Opportunity of 1.47 kWh
WLLS1 | RTU46 | 2024-04-06 15:59:59 | Compressor run ignoring free cooling Opportunity of 1.47 kWh
WLLS1 | RTU46 | 2024-04-06 16:15:02 | Compressor run ignoring free cooling Opportunity of 1.47 kWh
WLLS1 | RTU46 | 2024-04-07 15:44:52 | Compressor run ignoring free cooling Opportunity of 3.58 kWh
WLLS1 | RTU46 | 2024-04-07 15:59:56 | Compressor run ignoring free cooling Opportunity of 3.59 kWh
WLLS1 | RTU46 | 2024-04-07 16:14:59 | Compressor run ignoring free cooling Opportunity of 3.58 kWh
WLLS1 | RTU46 | 2024-04-07 16:30:01 | Compressor run ignoring free cooling Opportunity of 3.56 kWh
WLLS1 | RTU46 | 2024-04-07 16:45:04 | Compressor run ignoring free cooling Opportunity of 3.51 kWh
WLLS1 | RTU46 | 2024-04-19 21:44:57 | Compressor run ignoring free cooling Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-04-19 22:59:55 | Compressor run ignoring free cooling Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-04-22 16:44:51 | Compressor run ignoring free cooling Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-04-22 17:59:52 | Compressor run ignoring free cooling Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-04-25 19:29:55 | Compressor run ignoring free cooling Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-04-26 16:29:55 | Compressor run ignoring free cooling Opportunity of 3.55 kWh
WLLS1 | RTU46 | 2024-04-26 18:44:52 | Compressor run ignoring free cooling Opportunity of 3.49 kWh
WLLS1 | RTU46 | 2024-04-26 19:59:51 | Compressor run ignoring free cooling Opportunity of 1.41 kWh
WLLS1 | RTU46 | 2024-04-27 21:44:52 | Compressor run ignoring free cooling Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-05-06 21:29:57 | Compressor run ignoring free cooling Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-10 19:15:02 | Compressor run ignoring free cooling Opportunity of 3.55 kWh
WLLS1 | RTU46 | 2024-05-10 20:59:58 | Compressor run ignoring free cooling Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-11 19:00:00 | Compressor run ignoring free cooling Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-13 19:00:03 | Compressor run ignoring free cooling Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-13 19:15:03 | Compressor run ignoring free cooling Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-15 22:30:05 | Compressor run ignoring free cooling Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-15 22:45:04 | Compressor run ignoring free cooling Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-15 23:00:03 | Compressor run ignoring free cooling Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-15 23:15:02 | Compressor run ignoring free cooling Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-18 18:14:52 | Compressor run ignoring free cooling Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-05-19 21:44:55 | Compressor run ignoring free cooling Opportunity of 1.46 kWh
WLLS1 | RTU46 | 2024-05-20 21:44:55 | Compressor run ignoring free cooling Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-20 22:59:55 | Compressor run ignoring free cooling Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-22 21:44:56 | Compressor run ignoring free cooling Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-23 06:14:50 | Compressor run ignoring free cooling Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-23 20:14:56 | Compressor run ignoring free cooling Opportunity of 3.55 kWh
WLLS1 | RTU46 | 2024-05-24 17:44:52 | Compressor run ignoring free cooling Opportunity of 3.61 kWh
WLLS1 | RTU46 | 2024-05-25 17:59:51 | Compressor run ignoring free cooling Opportunity of 3.49 kWh
WLLS1 | RTU46 | 2024-05-25 18:14:54 | Compressor run ignoring free cooling Opportunity of 3.33 kWh
WLLS1 | RTU46 | 2024-05-25 18:29:58 | Compressor run ignoring free cooling Opportunity of 3.40 kWh
WLLS1 | RTU46 | 2024-05-29 21:14:52 | Compressor run ignoring free cooling Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-29 21:29:55 | Compressor run ignoring free cooling Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-31 21:14:54 | Compressor run ignoring free cooling Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-31 21:29:57 | Compressor run ignoring free cooling Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-02-10 11:00:05 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-03-07 14:15:05 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-03-07 14:30:00 | Compressor run ignoring free heating Opportunity of 1.47 kWh
WLLS1 | RTU46 | 2024-03-07 16:45:03 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-03-07 16:59:59 | Compressor run ignoring free heating Opportunity of 1.46 kWh
WLLS1 | RTU46 | 2024-03-13 17:15:00 | Compressor run ignoring free heating Opportunity of 1.46 kWh
WLLS1 | RTU46 | 2024-03-15 17:30:00 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-03-15 17:44:56 | Compressor run ignoring free heating Opportunity of 1.46 kWh
WLLS1 | RTU46 | 2024-03-16 14:00:02 | Compressor run ignoring free heating Opportunity of 1.47 kWh
WLLS1 | RTU46 | 2024-03-17 18:00:07 | Compressor run ignoring free heating Opportunity of 1.46 kWh
WLLS1 | RTU46 | 2024-03-17 18:15:02 | Compressor run ignoring free heating Opportunity of 1.46 kWh
WLLS1 | RTU46 | 2024-03-17 18:29:58 | Compressor run ignoring free heating Opportunity of 1.49 kWh
WLLS1 | RTU46 | 2024-03-20 13:15:03 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-03-20 13:29:59 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-03-22 15:14:54 | Compressor run ignoring free heating Opportunity of 1.46 kWh
WLLS1 | RTU46 | 2024-03-30 13:29:56 | Compressor run ignoring free heating Opportunity of 1.52 kWh
WLLS1 | RTU46 | 2024-03-30 13:44:59 | Compressor run ignoring free heating Opportunity of 1.47 kWh
WLLS1 | RTU46 | 2024-03-30 14:00:02 | Compressor run ignoring free heating Opportunity of 1.48 kWh
WLLS1 | RTU46 | 2024-03-30 19:59:50 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-03-31 12:29:52 | Compressor run ignoring free heating Opportunity of 1.55 kWh
WLLS1 | RTU46 | 2024-03-31 12:44:57 | Compressor run ignoring free heating Opportunity of 1.52 kWh
WLLS1 | RTU46 | 2024-03-31 13:00:00 | Compressor run ignoring free heating Opportunity of 1.51 kWh
WLLS1 | RTU46 | 2024-03-31 19:44:59 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-04-01 21:44:54 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-04-01 21:59:58 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-04-01 22:15:03 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-04-02 20:14:59 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-04-02 20:30:02 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-04-20 13:44:56 | Compressor run ignoring free heating Opportunity of 1.46 kWh
WLLS1 | RTU46 | 2024-04-20 19:44:51 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-04-20 20:59:51 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-04-20 22:14:52 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-04-25 13:14:51 | Compressor run ignoring free heating Opportunity of 1.47 kWh
WLLS1 | RTU46 | 2024-04-27 17:59:50 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-04-27 19:14:53 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-04-28 13:44:51 | Compressor run ignoring free heating Opportunity of 1.47 kWh
WLLS1 | RTU46 | 2024-04-28 14:59:52 | Compressor run ignoring free heating Opportunity of 1.49 kWh
WLLS1 | RTU46 | 2024-04-29 21:44:52 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-04-30 21:59:55 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-04-30 23:14:52 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-05-01 11:14:53 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-06 11:30:07 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-07 10:59:55 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-08 22:59:50 | Compressor run ignoring free heating Opportunity of 1.41 kWh
WLLS1 | RTU46 | 2024-05-09 08:29:51 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-05-09 11:44:51 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-09 21:15:04 | Compressor run ignoring free heating Opportunity of 1.46 kWh
WLLS1 | RTU46 | 2024-05-09 21:30:04 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-05-09 21:45:04 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-09 22:00:02 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-09 22:15:02 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-09 22:30:02 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-09 22:45:00 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-09 22:59:58 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-09 23:14:58 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-11 13:45:06 | Compressor run ignoring free heating Opportunity of 1.47 kWh
WLLS1 | RTU46 | 2024-05-11 13:59:58 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-13 12:14:55 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-05-13 12:29:54 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-13 13:14:49 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-13 19:44:59 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-13 19:59:57 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-05-13 20:14:57 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-13 20:29:56 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-05-13 20:44:55 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-05-13 21:29:52 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-15 15:14:55 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-05-15 15:29:54 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-15 15:44:52 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-17 11:29:54 | Compressor run ignoring free heating Opportunity of 1.41 kWh
WLLS1 | RTU46 | 2024-05-17 12:44:55 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-17 13:59:54 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-17 15:14:53 | Compressor run ignoring free heating Opportunity of 1.41 kWh
WLLS1 | RTU46 | 2024-05-17 20:14:52 | Compressor run ignoring free heating Opportunity of 1.41 kWh
WLLS1 | RTU46 | 2024-05-17 21:44:55 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-19 15:44:51 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-05-19 18:14:57 | Compressor run ignoring free heating Opportunity of 1.47 kWh
WLLS1 | RTU46 | 2024-05-19 19:14:50 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-05-20 13:14:54 | Compressor run ignoring free heating Opportunity of 1.52 kWh
WLLS1 | RTU46 | 2024-05-21 11:45:00 | Compressor run ignoring free heating Opportunity of 1.41 kWh
WLLS1 | RTU46 | 2024-05-21 12:00:02 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-21 20:29:54 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-21 20:44:56 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-21 20:59:59 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-23 09:44:52 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-23 09:59:56 | Compressor run ignoring free heating Opportunity of 1.47 kWh
WLLS1 | RTU46 | 2024-05-23 10:15:00 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-05-23 22:59:54 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-23 23:14:57 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-24 07:29:56 | Compressor run ignoring free heating Opportunity of 1.41 kWh
WLLS1 | RTU46 | 2024-05-24 07:45:02 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-24 08:00:04 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-24 10:59:58 | Compressor run ignoring free heating Opportunity of 1.45 kWh
WLLS1 | RTU46 | 2024-05-24 11:15:00 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-24 11:30:02 | Compressor run ignoring free heating Opportunity of 1.46 kWh
WLLS1 | RTU46 | 2024-05-24 20:59:54 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-24 21:15:00 | Compressor run ignoring free heating Opportunity of 1.39 kWh
WLLS1 | RTU46 | 2024-05-25 21:14:52 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-25 21:29:57 | Compressor run ignoring free heating Opportunity of 1.41 kWh
WLLS1 | RTU46 | 2024-05-25 21:45:00 | Compressor run ignoring free heating Opportunity of 1.41 kWh
WLLS1 | RTU46 | 2024-05-25 22:00:03 | Compressor run ignoring free heating Opportunity of 1.39 kWh
WLLS1 | RTU46 | 2024-05-26 21:15:01 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-27 09:44:51 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-27 09:59:53 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-27 10:14:58 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-27 10:30:01 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-27 10:45:04 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-27 13:14:51 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-27 13:29:55 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-27 13:44:57 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-27 13:59:59 | Compressor run ignoring free heating Opportunity of 1.42 kWh
WLLS1 | RTU46 | 2024-05-27 14:15:02 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU46 | 2024-05-27 16:59:52 | Compressor run ignoring free heating Opportunity of 1.46 kWh
WLLS1 | RTU46 | 2024-05-29 10:44:58 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-29 11:00:03 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-29 22:00:00 | Compressor run ignoring free heating Opportunity of 1.44 kWh
WLLS1 | RTU46 | 2024-05-29 22:15:03 | Compressor run ignoring free heating Opportunity of 1.43 kWh
WLLS1 | RTU47 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU47 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU47 | 2024-05-31 17:45:02 | No findings on Compressor being run ignoring free cooling Opportunity
WLLS1 | RTU47 | 2024-05-31 17:45:02 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU5 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU5 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU5 | 2024-05-31 20:44:56 | No findings on Compressor being run ignoring free cooling Opportunity
WLLS1 | RTU5 | 2024-05-31 20:44:56 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU6 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU6 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU6 | 2024-01-03 07:59:59 | Compressor run ignoring free cooling Opportunity of 2.03 kWh
WLLS1 | RTU6 | 2024-01-03 08:14:53 | Compressor run ignoring free cooling Opportunity of 2.01 kWh
WLLS1 | RTU6 | 2024-01-05 07:15:00 | Compressor run ignoring free cooling Opportunity of 2.04 kWh
WLLS1 | RTU6 | 2024-01-05 07:29:55 | Compressor run ignoring free cooling Opportunity of 2.06 kWh
WLLS1 | RTU6 | 2024-01-05 09:29:59 | Compressor run ignoring free cooling Opportunity of 2.04 kWh
WLLS1 | RTU6 | 2024-01-05 09:44:54 | Compressor run ignoring free cooling Opportunity of 2.06 kWh
WLLS1 | RTU6 | 2024-01-05 12:00:01 | Compressor run ignoring free cooling Opportunity of 2.05 kWh
WLLS1 | RTU6 | 2024-01-05 12:14:56 | Compressor run ignoring free cooling Opportunity of 2.07 kWh
WLLS1 | RTU6 | 2024-01-06 07:30:00 | Compressor run ignoring free cooling Opportunity of 2.06 kWh
WLLS1 | RTU6 | 2024-01-06 10:00:01 | Compressor run ignoring free cooling Opportunity of 2.03 kWh
WLLS1 | RTU6 | 2024-01-08 07:14:59 | Compressor run ignoring free cooling Opportunity of 2.04 kWh
WLLS1 | RTU6 | 2024-01-08 09:30:01 | Compressor run ignoring free cooling Opportunity of 2.04 kWh
WLLS1 | RTU6 | 2024-01-08 09:44:56 | Compressor run ignoring free cooling Opportunity of 2.03 kWh
WLLS1 | RTU6 | 2024-01-08 09:59:51 | Compressor run ignoring free cooling Opportunity of 2.03 kWh
WLLS1 | RTU6 | 2024-01-09 06:15:00 | Compressor run ignoring free cooling Opportunity of 2.05 kWh
WLLS1 | RTU6 | 2024-01-09 06:29:56 | Compressor run ignoring free cooling Opportunity of 2.07 kWh
WLLS1 | RTU6 | 2024-01-11 05:45:00 | Compressor run ignoring free cooling Opportunity of 2.01 kWh
WLLS1 | RTU6 | 2024-01-11 05:59:57 | Compressor run ignoring free cooling Opportunity of 2.01 kWh
WLLS1 | RTU6 | 2024-01-11 09:00:00 | Compressor run ignoring free cooling Opportunity of 2.02 kWh
WLLS1 | RTU6 | 2024-01-11 09:14:57 | Compressor run ignoring free cooling Opportunity of 2.03 kWh
WLLS1 | RTU6 | 2024-01-12 05:14:52 | Compressor run ignoring free cooling Opportunity of 2.06 kWh
WLLS1 | RTU6 | 2024-01-12 05:29:53 | Compressor run ignoring free cooling Opportunity of 2.05 kWh
WLLS1 | RTU6 | 2024-01-12 05:44:53 | Compressor run ignoring free cooling Opportunity of 2.05 kWh
WLLS1 | RTU6 | 2024-01-12 05:59:54 | Compressor run ignoring free cooling Opportunity of 2.02 kWh
WLLS1 | RTU6 | 2024-01-12 06:14:58 | Compressor run ignoring free cooling Opportunity of 2.04 kWh
WLLS1 | RTU6 | 2024-01-14 06:29:51 | Compressor run ignoring free cooling Opportunity of 2.06 kWh
WLLS1 | RTU6 | 2024-01-14 06:44:51 | Compressor run ignoring free cooling Opportunity of 2.04 kWh
WLLS1 | RTU6 | 2024-01-14 06:59:51 | Compressor run ignoring free cooling Opportunity of 2.04 kWh
WLLS1 | RTU6 | 2024-01-14 07:14:52 | Compressor run ignoring free cooling Opportunity of 2.04 kWh
WLLS1 | RTU6 | 2024-01-14 07:29:53 | Compressor run ignoring free cooling Opportunity of 2.04 kWh
WLLS1 | RTU6 | 2024-01-14 07:44:53 | Compressor run ignoring free cooling Opportunity of 2.07 kWh
WLLS1 | RTU6 | 2024-01-14 07:59:53 | Compressor run ignoring free cooling Opportunity of 2.09 kWh
WLLS1 | RTU6 | 2024-01-14 08:14:53 | Compressor run ignoring free cooling Opportunity of 2.09 kWh
WLLS1 | RTU6 | 2024-01-14 08:29:55 | Compressor run ignoring free cooling Opportunity of 2.10 kWh
WLLS1 | RTU6 | 2024-01-14 08:44:56 | Compressor run ignoring free cooling Opportunity of 2.06 kWh
WLLS1 | RTU6 | 2024-01-14 08:59:57 | Compressor run ignoring free cooling Opportunity of 2.06 kWh
WLLS1 | RTU6 | 2024-01-14 09:14:57 | Compressor run ignoring free cooling Opportunity of 2.10 kWh
WLLS1 | RTU6 | 2024-01-14 09:29:59 | Compressor run ignoring free cooling Opportunity of 2.09 kWh
WLLS1 | RTU6 | 2024-01-14 09:45:01 | Compressor run ignoring free cooling Opportunity of 2.06 kWh
WLLS1 | RTU6 | 2024-01-14 10:00:01 | Compressor run ignoring free cooling Opportunity of 2.10 kWh
WLLS1 | RTU6 | 2024-01-17 09:29:57 | Compressor run ignoring free cooling Opportunity of 2.06 kWh
WLLS1 | RTU6 | 2024-01-17 11:29:57 | Compressor run ignoring free cooling Opportunity of 2.03 kWh
WLLS1 | RTU6 | 2024-01-17 11:44:51 | Compressor run ignoring free cooling Opportunity of 2.03 kWh
WLLS1 | RTU6 | 2024-01-17 13:45:01 | Compressor run ignoring free cooling Opportunity of 2.07 kWh
WLLS1 | RTU6 | 2024-01-17 15:44:59 | Compressor run ignoring free cooling Opportunity of 2.05 kWh
WLLS1 | RTU6 | 2024-01-17 17:59:57 | Compressor run ignoring free cooling Opportunity of 2.09 kWh
WLLS1 | RTU6 | 2024-01-17 21:44:56 | Compressor run ignoring free cooling Opportunity of 2.04 kWh
WLLS1 | RTU6 | 2024-01-18 05:30:02 | Compressor run ignoring free cooling Opportunity of 1.91 kWh
WLLS1 | RTU6 | 2024-01-18 05:44:57 | Compressor run ignoring free cooling Opportunity of 1.92 kWh
WLLS1 | RTU6 | 2024-03-04 15:15:01 | Compressor run ignoring free cooling Opportunity of 3.98 kWh
WLLS1 | RTU6 | 2024-03-04 15:29:55 | Compressor run ignoring free cooling Opportunity of 4.22 kWh
WLLS1 | RTU6 | 2024-03-04 17:30:00 | Compressor run ignoring free cooling Opportunity of 3.88 kWh
WLLS1 | RTU6 | 2024-03-07 12:29:58 | Compressor run ignoring free cooling Opportunity of 4.38 kWh
WLLS1 | RTU6 | 2024-03-07 14:59:59 | Compressor run ignoring free cooling Opportunity of 4.24 kWh
WLLS1 | RTU6 | 2024-03-07 17:30:01 | Compressor run ignoring free cooling Opportunity of 4.23 kWh
WLLS1 | RTU6 | 2024-03-07 17:44:56 | Compressor run ignoring free cooling Opportunity of 4.19 kWh
WLLS1 | RTU6 | 2024-03-08 16:30:01 | Compressor run ignoring free cooling Opportunity of 2.24 kWh
WLLS1 | RTU6 | 2024-03-08 16:44:56 | Compressor run ignoring free cooling Opportunity of 4.15 kWh
WLLS1 | RTU6 | 2024-03-13 20:14:57 | Compressor run ignoring free cooling Opportunity of 3.91 kWh
WLLS1 | RTU6 | 2024-03-14 21:59:58 | Compressor run ignoring free cooling Opportunity of 4.20 kWh
WLLS1 | RTU6 | 2024-03-14 22:14:55 | Compressor run ignoring free cooling Opportunity of 4.13 kWh
WLLS1 | RTU6 | 2024-03-15 20:45:00 | Compressor run ignoring free cooling Opportunity of 4.15 kWh
WLLS1 | RTU6 | 2024-03-16 17:29:58 | Compressor run ignoring free cooling Opportunity of 2.22 kWh
WLLS1 | RTU6 | 2024-03-16 19:59:56 | Compressor run ignoring free cooling Opportunity of 4.22 kWh
WLLS1 | RTU6 | 2024-03-17 18:59:59 | Compressor run ignoring free cooling Opportunity of 4.36 kWh
WLLS1 | RTU6 | 2024-03-17 19:14:56 | Compressor run ignoring free cooling Opportunity of 2.20 kWh
WLLS1 | RTU6 | 2024-03-20 18:15:01 | Compressor run ignoring free cooling Opportunity of 4.15 kWh
WLLS1 | RTU6 | 2024-03-20 18:29:59 | Compressor run ignoring free cooling Opportunity of 4.24 kWh
WLLS1 | RTU6 | 2024-03-20 18:44:58 | Compressor run ignoring free cooling Opportunity of 4.20 kWh
WLLS1 | RTU6 | 2024-03-20 18:59:55 | Compressor run ignoring free cooling Opportunity of 4.22 kWh
WLLS1 | RTU6 | 2024-03-20 19:14:52 | Compressor run ignoring free cooling Opportunity of 4.19 kWh
WLLS1 | RTU6 | 2024-03-30 22:59:48 | Compressor run ignoring free cooling Opportunity of 4.16 kWh
WLLS1 | RTU6 | 2024-03-30 23:14:50 | Compressor run ignoring free cooling Opportunity of 4.05 kWh
WLLS1 | RTU6 | 2024-03-31 21:59:51 | Compressor run ignoring free cooling Opportunity of 4.36 kWh
WLLS1 | RTU6 | 2024-03-31 22:14:55 | Compressor run ignoring free cooling Opportunity of 4.27 kWh
WLLS1 | RTU6 | 2024-04-01 20:59:54 | Compressor run ignoring free cooling Opportunity of 2.23 kWh
WLLS1 | RTU6 | 2024-04-01 21:14:57 | Compressor run ignoring free cooling Opportunity of 4.43 kWh
WLLS1 | RTU6 | 2024-04-02 05:14:50 | Compressor run ignoring free cooling Opportunity of 2.19 kWh
WLLS1 | RTU6 | 2024-04-02 05:29:53 | Compressor run ignoring free cooling Opportunity of 4.24 kWh
WLLS1 | RTU6 | 2024-04-02 05:44:57 | Compressor run ignoring free cooling Opportunity of 2.19 kWh
WLLS1 | RTU6 | 2024-04-03 06:59:50 | Compressor run ignoring free cooling Opportunity of 2.17 kWh
WLLS1 | RTU6 | 2024-04-03 07:14:54 | Compressor run ignoring free cooling Opportunity of 4.35 kWh
WLLS1 | RTU6 | 2024-04-03 07:29:56 | Compressor run ignoring free cooling Opportunity of 2.21 kWh
WLLS1 | RTU6 | 2024-04-19 19:59:52 | Compressor run ignoring free cooling Opportunity of 2.21 kWh
WLLS1 | RTU6 | 2024-04-19 21:14:50 | Compressor run ignoring free cooling Opportunity of 2.23 kWh
WLLS1 | RTU6 | 2024-04-23 19:29:50 | Compressor run ignoring free cooling Opportunity of 4.28 kWh
WLLS1 | RTU6 | 2024-04-24 14:59:51 | Compressor run ignoring free cooling Opportunity of 4.26 kWh
WLLS1 | RTU6 | 2024-04-24 16:14:49 | Compressor run ignoring free cooling Opportunity of 4.26 kWh
WLLS1 | RTU6 | 2024-04-26 20:59:52 | Compressor run ignoring free cooling Opportunity of 2.24 kWh
WLLS1 | RTU6 | 2024-04-28 19:44:52 | Compressor run ignoring free cooling Opportunity of 4.56 kWh
WLLS1 | RTU6 | 2024-04-28 22:59:49 | Compressor run ignoring free cooling Opportunity of 2.23 kWh
WLLS1 | RTU6 | 2024-05-06 20:59:51 | Compressor run ignoring free cooling Opportunity of 4.43 kWh
WLLS1 | RTU6 | 2024-05-06 22:14:52 | Compressor run ignoring free cooling Opportunity of 4.46 kWh
WLLS1 | RTU6 | 2024-05-10 21:29:55 | Compressor run ignoring free cooling Opportunity of 3.87 kWh
WLLS1 | RTU6 | 2024-05-10 23:00:00 | Compressor run ignoring free cooling Opportunity of 3.83 kWh
WLLS1 | RTU6 | 2024-05-11 14:29:55 | Compressor run ignoring free cooling Opportunity of 3.93 kWh
WLLS1 | RTU6 | 2024-05-11 19:29:58 | Compressor run ignoring free cooling Opportunity of 3.91 kWh
WLLS1 | RTU6 | 2024-05-11 21:15:01 | Compressor run ignoring free cooling Opportunity of 3.86 kWh
WLLS1 | RTU6 | 2024-05-12 21:30:00 | Compressor run ignoring free cooling Opportunity of 3.88 kWh
WLLS1 | RTU6 | 2024-05-13 22:00:00 | Compressor run ignoring free cooling Opportunity of 3.89 kWh
WLLS1 | RTU6 | 2024-05-13 22:15:00 | Compressor run ignoring free cooling Opportunity of 2.14 kWh
WLLS1 | RTU6 | 2024-05-13 22:29:58 | Compressor run ignoring free cooling Opportunity of 3.91 kWh
WLLS1 | RTU6 | 2024-05-13 22:44:56 | Compressor run ignoring free cooling Opportunity of 2.16 kWh
WLLS1 | RTU6 | 2024-05-13 22:59:56 | Compressor run ignoring free cooling Opportunity of 3.88 kWh
WLLS1 | RTU6 | 2024-05-13 23:14:55 | Compressor run ignoring free cooling Opportunity of 2.15 kWh
WLLS1 | RTU6 | 2024-05-14 06:45:02 | Compressor run ignoring free cooling Opportunity of 3.81 kWh
WLLS1 | RTU6 | 2024-05-14 07:00:01 | Compressor run ignoring free cooling Opportunity of 2.17 kWh
WLLS1 | RTU6 | 2024-05-14 08:29:52 | Compressor run ignoring free cooling Opportunity of 2.17 kWh
WLLS1 | RTU6 | 2024-05-14 09:14:49 | Compressor run ignoring free cooling Opportunity of 2.19 kWh
WLLS1 | RTU6 | 2024-05-14 16:59:59 | Compressor run ignoring free cooling Opportunity of 2.19 kWh
WLLS1 | RTU6 | 2024-05-14 17:14:58 | Compressor run ignoring free cooling Opportunity of 3.95 kWh
WLLS1 | RTU6 | 2024-05-14 17:29:55 | Compressor run ignoring free cooling Opportunity of 2.19 kWh
WLLS1 | RTU6 | 2024-05-14 17:44:55 | Compressor run ignoring free cooling Opportunity of 3.89 kWh
WLLS1 | RTU6 | 2024-05-14 17:59:56 | Compressor run ignoring free cooling Opportunity of 3.90 kWh
WLLS1 | RTU6 | 2024-05-14 18:14:54 | Compressor run ignoring free cooling Opportunity of 3.91 kWh
WLLS1 | RTU6 | 2024-05-14 18:29:54 | Compressor run ignoring free cooling Opportunity of 3.88 kWh
WLLS1 | RTU6 | 2024-05-14 18:44:52 | Compressor run ignoring free cooling Opportunity of 2.20 kWh
WLLS1 | RTU6 | 2024-05-14 18:59:52 | Compressor run ignoring free cooling Opportunity of 3.95 kWh
WLLS1 | RTU6 | 2024-05-14 19:14:49 | Compressor run ignoring free cooling Opportunity of 3.93 kWh
WLLS1 | RTU6 | 2024-05-17 06:14:49 | Compressor run ignoring free cooling Opportunity of 3.84 kWh
WLLS1 | RTU6 | 2024-05-17 18:44:50 | Compressor run ignoring free cooling Opportunity of 3.94 kWh
WLLS1 | RTU6 | 2024-05-17 21:14:48 | Compressor run ignoring free cooling Opportunity of 2.14 kWh
WLLS1 | RTU6 | 2024-05-17 22:29:50 | Compressor run ignoring free cooling Opportunity of 3.90 kWh
WLLS1 | RTU6 | 2024-05-18 08:14:52 | Compressor run ignoring free cooling Opportunity of 3.90 kWh
WLLS1 | RTU6 | 2024-05-18 21:29:51 | Compressor run ignoring free cooling Opportunity of 2.19 kWh
WLLS1 | RTU6 | 2024-05-18 22:44:52 | Compressor run ignoring free cooling Opportunity of 3.86 kWh
WLLS1 | RTU6 | 2024-05-19 10:44:52 | Compressor run ignoring free cooling Opportunity of 2.21 kWh
WLLS1 | RTU6 | 2024-05-19 17:44:50 | Compressor run ignoring free cooling Opportunity of 3.98 kWh
WLLS1 | RTU6 | 2024-05-19 22:29:49 | Compressor run ignoring free cooling Opportunity of 3.86 kWh
WLLS1 | RTU6 | 2024-05-21 22:59:53 | Compressor run ignoring free cooling Opportunity of 3.90 kWh
WLLS1 | RTU6 | 2024-05-21 23:14:56 | Compressor run ignoring free cooling Opportunity of 2.16 kWh
WLLS1 | RTU6 | 2024-05-22 05:14:57 | Compressor run ignoring free cooling Opportunity of 2.17 kWh
WLLS1 | RTU6 | 2024-05-23 05:14:49 | Compressor run ignoring free cooling Opportunity of 3.85 kWh
WLLS1 | RTU6 | 2024-05-23 05:29:52 | Compressor run ignoring free cooling Opportunity of 5.67 kWh
WLLS1 | RTU6 | 2024-05-23 05:44:55 | Compressor run ignoring free cooling Opportunity of 3.62 kWh
WLLS1 | RTU6 | 2024-05-23 21:59:51 | Compressor run ignoring free cooling Opportunity of 2.13 kWh
WLLS1 | RTU6 | 2024-05-23 22:14:54 | Compressor run ignoring free cooling Opportunity of 3.91 kWh
WLLS1 | RTU6 | 2024-05-23 22:29:57 | Compressor run ignoring free cooling Opportunity of 2.13 kWh
WLLS1 | RTU6 | 2024-05-24 06:14:50 | Compressor run ignoring free cooling Opportunity of 3.87 kWh
WLLS1 | RTU6 | 2024-05-24 06:29:53 | Compressor run ignoring free cooling Opportunity of 2.14 kWh
WLLS1 | RTU6 | 2024-05-24 06:44:56 | Compressor run ignoring free cooling Opportunity of 3.87 kWh
WLLS1 | RTU6 | 2024-05-24 19:59:50 | Compressor run ignoring free cooling Opportunity of 3.95 kWh
WLLS1 | RTU6 | 2024-05-24 20:14:54 | Compressor run ignoring free cooling Opportunity of 3.97 kWh
WLLS1 | RTU6 | 2024-05-24 20:29:58 | Compressor run ignoring free cooling Opportunity of 3.96 kWh
WLLS1 | RTU6 | 2024-05-24 22:44:48 | Compressor run ignoring free cooling Opportunity of 3.87 kWh
WLLS1 | RTU6 | 2024-05-24 22:59:53 | Compressor run ignoring free cooling Opportunity of 2.12 kWh
WLLS1 | RTU6 | 2024-05-25 20:14:51 | Compressor run ignoring free cooling Opportunity of 2.12 kWh
WLLS1 | RTU6 | 2024-05-25 20:29:56 | Compressor run ignoring free cooling Opportunity of 3.84 kWh
WLLS1 | RTU6 | 2024-05-25 20:44:58 | Compressor run ignoring free cooling Opportunity of 2.12 kWh
WLLS1 | RTU6 | 2024-05-27 05:14:49 | Compressor run ignoring free cooling Opportunity of 3.79 kWh
WLLS1 | RTU6 | 2024-05-27 05:29:54 | Compressor run ignoring free cooling Opportunity of 5.60 kWh
WLLS1 | RTU6 | 2024-05-27 05:44:57 | Compressor run ignoring free cooling Opportunity of 3.60 kWh
WLLS1 | RTU6 | 2024-05-27 08:44:51 | Compressor run ignoring free cooling Opportunity of 3.90 kWh
WLLS1 | RTU6 | 2024-05-27 08:59:54 | Compressor run ignoring free cooling Opportunity of 3.91 kWh
WLLS1 | RTU6 | 2024-05-27 09:14:57 | Compressor run ignoring free cooling Opportunity of 2.17 kWh
WLLS1 | RTU6 | 2024-05-27 23:14:49 | Compressor run ignoring free cooling Opportunity of 3.87 kWh
WLLS1 | RTU6 | 2024-05-28 05:14:54 | Compressor run ignoring free cooling Opportunity of 2.15 kWh
WLLS1 | RTU6 | 2024-05-29 20:44:54 | Compressor run ignoring free cooling Opportunity of 4.06 kWh
WLLS1 | RTU6 | 2024-05-30 05:14:49 | Compressor run ignoring free cooling Opportunity of 2.16 kWh
WLLS1 | RTU6 | 2024-05-30 05:29:54 | Compressor run ignoring free cooling Opportunity of 3.77 kWh
WLLS1 | RTU6 | 2024-05-30 22:44:50 | Compressor run ignoring free cooling Opportunity of 2.16 kWh
WLLS1 | RTU6 | 2024-05-30 22:59:53 | Compressor run ignoring free cooling Opportunity of 3.79 kWh
WLLS1 | RTU6 | 2024-05-30 23:14:55 | Compressor run ignoring free cooling Opportunity of 3.02 kWh
WLLS1 | RTU6 | 2024-05-31 19:59:48 | Compressor run ignoring free cooling Opportunity of 3.93 kWh
WLLS1 | RTU6 | 2024-05-31 20:14:51 | Compressor run ignoring free cooling Opportunity of 3.88 kWh
WLLS1 | RTU6 | 2024-05-31 20:44:56 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU8 | No_Time_stamp | No findings on Unit Quick ON/Off within 15 min
WLLS1 | RTU8 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU8 | 2024-05-31 20:44:56 | No findings on Compressor being run ignoring free cooling Opportunity
WLLS1 | RTU8 | 2024-05-31 20:44:56 | No findings on heating by ignoring free heating Opportunity
WLLS1 | RTU9 | 2024-04-02 09:15:01 | Unit Quick ON/Off within 15 min
WLLS1 | RTU9 | 2024-04-02 11:59:54 | Unit Quick ON/Off within 15 min
WLLS1 | RTU9 | 2024-05-23 12:29:56 | Unit Quick ON/Off within 15 min
WLLS1 | RTU9 | 2024-05-31 13:14:57 | Unit Quick ON/Off within 15 min
WLLS1 | RTU9 | No_Time_stamp | No findings on Short Cycling Detected
WLLS1 | RTU9 | 2024-01-06 10:00:05 | Compressor run ignoring free cooling Opportunity of 6.72 kWh
WLLS1 | RTU9 | 2024-01-06 10:14:59 | Compressor run ignoring free cooling Opportunity of 7.01 kWh
WLLS1 | RTU9 | 2024-01-06 12:15:02 | Compressor run ignoring free cooling Opportunity of 7.14 kWh
WLLS1 | RTU9 | 2024-01-06 12:29:57 | Compressor run ignoring free cooling Opportunity of 11.55 kWh
WLLS1 | RTU9 | 2024-01-06 14:59:58 | Compressor run ignoring free cooling Opportunity of 7.30 kWh
WLLS1 | RTU9 | 2024-01-10 06:59:58 | Compressor run ignoring free cooling Opportunity of 6.92 kWh
WLLS1 | RTU9 | 2024-01-10 08:00:05 | Compressor run ignoring free cooling Opportunity of 6.90 kWh
WLLS1 | RTU9 | 2024-01-10 16:00:05 | Compressor run ignoring free cooling Opportunity of 6.76 kWh
WLLS1 | RTU9 | 2024-03-04 15:15:05 | Compressor run ignoring free cooling Opportunity of 7.55 kWh
WLLS1 | RTU9 | 2024-03-05 05:44:55 | Compressor run ignoring free cooling Opportunity of 7.17 kWh
WLLS1 | RTU9 | 2024-03-05 10:00:05 | Compressor run ignoring free cooling Opportunity of 2.16 kWh
WLLS1 | RTU9 | 2024-03-13 20:29:58 | Compressor run ignoring free cooling Opportunity of 7.41 kWh
WLLS1 | RTU9 | 2024-03-15 15:45:03 | Compressor run ignoring free cooling Opportunity of 2.07 kWh
WLLS1 | RTU9 | 2024-03-15 15:59:58 | Compressor run ignoring free cooling Opportunity of 7.55 kWh
WLLS1 | RTU9 | 2024-03-15 18:15:00 | Compressor run ignoring free cooling Opportunity of 7.53 kWh
WLLS1 | RTU9 | 2024-03-15 20:45:04 | Compressor run ignoring free cooling Opportunity of 2.07 kWh
WLLS1 | RTU9 | 2024-03-16 17:44:57 | Compressor run ignoring free cooling Opportunity of 7.64 kWh
WLLS1 | RTU9 | 2024-03-20 19:14:55 | Compressor run ignoring free cooling Opportunity of 7.37 kWh
WLLS1 | RTU9 | 2024-03-31 22:14:59 | Compressor run ignoring free cooling Opportunity of 7.82 kWh
WLLS1 | RTU9 | 2024-04-01 20:59:58 | Compressor run ignoring free cooling Opportunity of 7.93 kWh
WLLS1 | RTU9 | 2024-04-02 08:44:54 | Compressor run ignoring free cooling Opportunity of 7.48 kWh
WLLS1 | RTU9 | 2024-04-03 06:29:48 | Compressor run ignoring free cooling Opportunity of 7.62 kWh
WLLS1 | RTU9 | 2024-04-08 15:14:48 | Compressor run ignoring free cooling Opportunity of 7.46 kWh
WLLS1 | RTU9 | 2024-04-19 11:14:55 | Compressor run ignoring free cooling Opportunity of 7.55 kWh
WLLS1 | RTU9 | 2024-04-19 21:14:54 | Compressor run ignoring free cooling Opportunity of 7.59 kWh
WLLS1 | RTU9 | 2024-04-20 20:29:48 | Compressor run ignoring free cooling Opportunity of 7.59 kWh
WLLS1 | RTU9 | 2024-04-21 05:59:47 | Compressor run ignoring free cooling Opportunity of 2.09 kWh
WLLS1 | RTU9 | 2024-04-22 18:44:50 | Compressor run ignoring free cooling Opportunity of 7.12 kWh
WLLS1 | RTU9 | 2024-04-24 14:59:55 | Compressor run ignoring free cooling Opportunity of 7.30 kWh
WLLS1 | RTU9 | 2024-04-26 13:29:53 | Compressor run ignoring free cooling Opportunity of 7.66 kWh
WLLS1 | RTU9 | 2024-04-26 19:29:48 | Compressor run ignoring free cooling Opportunity of 7.41 kWh
WLLS1 | RTU9 | 2024-04-26 20:59:55 | Compressor run ignoring free cooling Opportunity of 7.44 kWh
WLLS1 | RTU9 | 2024-04-27 19:59:49 | Compressor run ignoring free cooling Opportunity of 7.59 kWh
WLLS1 | RTU9 | 2024-04-28 19:44:55 | Compressor run ignoring free cooling Opportunity of 7.64 kWh
WLLS1 | RTU9 | 2024-04-28 21:59:52 | Compressor run ignoring free cooling Opportunity of 7.64 kWh
WLLS1 | RTU9 | 2024-04-29 21:14:50 | Compressor run ignoring free cooling Opportunity of 7.91 kWh
WLLS1 | RTU9 | 2024-04-29 22:29:49 | Compressor run ignoring free cooling Opportunity of 7.59 kWh
WLLS1 | RTU9 | 2024-04-30 21:29:50 | Compressor run ignoring free cooling Opportunity of 7.82 kWh
WLLS1 | RTU9 | 2024-05-01 05:44:48 | Compressor run ignoring free cooling Opportunity of 7.35 kWh
WLLS1 | RTU9 | 2024-05-04 22:30:05 | Compressor run ignoring free cooling Opportunity of 9.75 kWh
WLLS1 | RTU9 | 2024-05-07 06:44:50 | Compressor run ignoring free cooling Opportunity of 10.04 kWh
WLLS1 | RTU9 | 2024-05-10 23:14:56 | Compressor run ignoring free cooling Opportunity of 6.87 kWh
WLLS1 | RTU9 | 2024-05-11 14:29:58 | Compressor run ignoring free cooling Opportunity of 7.17 kWh
WLLS1 | RTU9 | 2024-05-11 19:30:01 | Compressor run ignoring free cooling Opportunity of 7.26 kWh
WLLS1 | RTU9 | 2024-05-12 19:59:57 | Compressor run ignoring free cooling Opportunity of 7.21 kWh
WLLS1 | RTU9 | 2024-05-12 21:44:56 | Compressor run ignoring free cooling Opportunity of 7.12 kWh
WLLS1 | RTU9 | 2024-05-12 23:15:01 | Compressor run ignoring free cooling Opportunity of 7.01 kWh
WLLS1 | RTU9 | 2024-05-13 22:00:04 | Compressor run ignoring free cooling Opportunity of 7.26 kWh
WLLS1 | RTU9 | 2024-05-13 22:15:04 | Compressor run ignoring free cooling Opportunity of 7.26 kWh
WLLS1 | RTU9 | 2024-05-14 06:45:06 | Compressor run ignoring free cooling Opportunity of 6.96 kWh
WLLS1 | RTU9 | 2024-05-14 08:29:55 | Compressor run ignoring free cooling Opportunity of 7.21 kWh
WLLS1 | RTU9 | 2024-05-14 09:29:52 | Compressor run ignoring free cooling Opportunity of 7.21 kWh
WLLS1 | RTU9 | 2024-05-14 09:44:50 | Compressor run ignoring free cooling Opportunity of 7.30 kWh
WLLS1 | RTU9 | 2024-05-14 09:59:51 | Compressor run ignoring free cooling Opportunity of 7.23 kWh
WLLS1 | RTU9 | 2024-05-14 10:14:49 | Compressor run ignoring free cooling Opportunity of 7.21 kWh
WLLS1 | RTU9 | 2024-05-14 17:29:59 | Compressor run ignoring free cooling Opportunity of 7.26 kWh
WLLS1 | RTU9 | 2024-05-14 17:44:59 | Compressor run ignoring free cooling Opportunity of 7.14 kWh
WLLS1 | RTU9 | 2024-05-15 19:29:47 | Compressor run ignoring free cooling Opportunity of 7.37 kWh
WLLS1 | RTU9 | 2024-05-17 21:14:52 | Compressor run ignoring free cooling Opportunity of 7.28 kWh
WLLS1 | RTU9 | 2024-05-18 05:29:48 | Compressor run ignoring free cooling Opportunity of 7.08 kWh
WLLS1 | RTU9 | 2024-05-18 06:44:49 | Compressor run ignoring free cooling Opportunity of 7.14 kWh
WLLS1 | RTU9 | 2024-05-18 18:59:52 | Compressor run ignoring free cooling Opportunity of 7.19 kWh
WLLS1 | RTU9 | 2024-05-18 22:29:47 | Compressor run ignoring free cooling Opportunity of 7.14 kWh
WLLS1 | RTU9 | 2024-05-19 17:44:54 | Compressor run ignoring free cooling Opportunity of 7.32 kWh
WLLS1 | RTU9 | 2024-05-19 19:59:48 | Compressor run ignoring free cooling Opportunity of 7.21 kWh
WLLS1 | RTU9 | 2024-05-19 21:14:51 | Compressor run ignoring free cooling Opportunity of 7.23 kWh
WLLS1 | RTU9 | 2024-05-20 21:14:50 | Compressor run ignoring free cooling Opportunity of 7.17 kWh
WLLS1 | RTU9 | 2024-05-21 22:29:49 | Compressor run ignoring free cooling Opportunity of 7.23 kWh
WLLS1 | RTU9 | 2024-05-21 22:44:52 | Compressor run ignoring free cooling Opportunity of 7.30 kWh
WLLS1 | RTU9 | 2024-05-22 05:15:00 | Compressor run ignoring free cooling Opportunity of 7.21 kWh
WLLS1 | RTU9 | 2024-05-22 23:14:49 | Compressor run ignoring free cooling Opportunity of 7.28 kWh
WLLS1 | RTU9 | 2024-05-23 05:14:53 | Compressor run ignoring free cooling Opportunity of 7.26 kWh
WLLS1 | RTU9 | 2024-05-23 05:29:55 | Compressor run ignoring free cooling Opportunity of 7.26 kWh
WLLS1 | RTU9 | 2024-05-23 05:44:58 | Compressor run ignoring free cooling Opportunity of 7.19 kWh
WLLS1 | RTU9 | 2024-05-23 21:29:48 | Compressor run ignoring free cooling Opportunity of 7.28 kWh
WLLS1 | RTU9 | 2024-05-24 06:29:56 | Compressor run ignoring free cooling Opportunity of 7.21 kWh
WLLS1 | RTU9 | 2024-05-24 06:45:00 | Compressor run ignoring free cooling Opportunity of 7.19 kWh
WLLS1 | RTU9 | 2024-05-24 20:30:01 | Compressor run ignoring free cooling Opportunity of 7.41 kWh
WLLS1 | RTU9 | 2024-05-24 22:14:46 | Compressor run ignoring free cooling Opportunity of 7.28 kWh
WLLS1 | RTU9 | 2024-05-25 19:44:46 | Compressor run ignoring free cooling Opportunity of 7.12 kWh
WLLS1 | RTU9 | 2024-05-25 19:59:52 | Compressor run ignoring free cooling Opportunity of 7.14 kWh
WLLS1 | RTU9 | 2024-05-25 20:14:55 | Compressor run ignoring free cooling Opportunity of 7.19 kWh
WLLS1 | RTU9 | 2024-05-25 20:29:59 | Compressor run ignoring free cooling Opportunity of 7.14 kWh
WLLS1 | RTU9 | 2024-05-25 20:45:02 | Compressor run ignoring free cooling Opportunity of 7.21 kWh
WLLS1 | RTU9 | 2024-05-25 23:14:47 | Compressor run ignoring free cooling Opportunity of 7.14 kWh
WLLS1 | RTU9 | 2024-05-27 05:14:53 | Compressor run ignoring free cooling Opportunity of 11.68 kWh
WLLS1 | RTU9 | 2024-05-27 05:29:58 | Compressor run ignoring free cooling Opportunity of 7.14 kWh
WLLS1 | RTU9 | 2024-05-27 08:14:47 | Compressor run ignoring free cooling Opportunity of 7.32 kWh
WLLS1 | RTU9 | 2024-05-27 08:29:51 | Compressor run ignoring free cooling Opportunity of 7.30 kWh
WLLS1 | RTU9 | 2024-05-27 22:44:48 | Compressor run ignoring free cooling Opportunity of 7.46 kWh
WLLS1 | RTU9 | 2024-05-28 05:14:58 | Compressor run ignoring free cooling Opportunity of 7.23 kWh
WLLS1 | RTU9 | 2024-05-29 20:44:58 | Compressor run ignoring free cooling Opportunity of 7.59 kWh
WLLS1 | RTU9 | 2024-05-30 05:14:53 | Compressor run ignoring free cooling Opportunity of 7.05 kWh
WLLS1 | RTU9 | 2024-05-30 09:14:54 | Compressor run ignoring free cooling Opportunity of 7.37 kWh
WLLS1 | RTU9 | 2024-05-30 22:59:56 | Compressor run ignoring free cooling Opportunity of 2.07 kWh
WLLS1 | RTU9 | 2024-05-30 23:14:59 | Compressor run ignoring free cooling Opportunity of 7.05 kWh
WLLS1 | RTU9 | 2024-05-31 19:44:48 | Compressor run ignoring free cooling Opportunity of 7.12 kWh
WLLS1 | RTU9 | 2024-05-31 19:59:52 | Compressor run ignoring free cooling Opportunity of 7.26 kWh
WLLS1 | RTU9 | 2024-05-31 20:14:55 | Compressor run ignoring free cooling Opportunity of 7.26 kWh
WLLS1 | RTU9 | 2024-05-03 18:00:05 | Compressor run ignoring free heating Opportunity of 2.09 kWh
WLLS1 | RTU9 | 2024-05-06 16:00:03 | Compressor run ignoring free heating Opportunity of 2.11 kWh
WLLS1 | RTU9 | 2024-05-06 17:14:55 | Compressor run ignoring free heating Opportunity of 2.09 kWh
WLLS1 | RTU9 | 2024-05-06 19:44:55 | Compressor run ignoring free heating Opportunity of 2.09 kWh
WLLS1 | RTU9 | 2024-05-07 12:59:55 | Compressor run ignoring free heating Opportunity of 2.07 kWh
WLLS1 | RTU9 | 2024-05-07 13:59:47 | Compressor run ignoring free heating Opportunity of 2.04 kWh
WLLS1 | RTU9 | 2024-05-07 15:14:50 | Compressor run ignoring free heating Opportunity of 2.07 kWh
WLLS1 | RTU9 | 2024-05-08 08:00:04 | Compressor run ignoring free heating Opportunity of 2.09 kWh